---
name: egc-coordination-control
version: 1.0.0
description: EGC协调控制逻辑知识库（FIP场景）
category: domains
tags: [EGC, FIP, 微网, 储能, 光伏]
allowed-tools: [Read, Write, Edit, Grep]
---

# EGC 协调控制（FIP）

## 这是什么？

FIP 是一种控制策略，用于让微电网：
- 光伏发电尽量自己用，不浪费
- 不从电网买电
- 多余的电要么存储能，要么送到电网

---

## 输入参数

| 参数 | 是什么 | 例子 |
|------|--------|------|
| bess_ap_setpoint | AIM发的指令（正=充电，负=放电，0=不管） | 100 / -50 / 0 |
| PV | 光伏现在发了多少电 | 50kW |
| plant_capacity | 场站总共能发多少 | 100kW |
| curtailment_percent | 限发比例（%） | 10% |
| SOC | 储能还有多少电（%) | 50% |

## 限值怎么算？

```
送出限值 = 场站容量 × 限发比例
例：100kW × 10% = 10kW
```

---

## 三条硬规则（最重要）

1. **不能从电网买电** — 输入限值=0
2. **不能用电网的电充电** — 只能用光伏充
3. **尽量用光伏** — 别浪费

---

## 怎么控制？

### 充电指令（bess_ap_setpoint > 0）

> 就是让它储能充电

1. 光伏先给储能充电
2. 剩下的电送到电网（不能超限值）
3. 再多就弃掉

### 待机指令（bess_ap_setpoint = 0）

> 就是让它别动

1. 光伏先送到电网
2. 剩下的给储能充电
3. 再多就弃掉

### 放电指令（bess_ap_setpoint < 0）

> 就是让它放电

| 光伏够不够 | 怎么做 |
|----------|--------|
| 光伏 ≥ 限值 | 送到电网满，储能不放电反而充电（反向） |
| 光伏 < 限值 | 光伏全送电网，不够的放电来补 |

---

## 特殊情况

| SOC状态 | 充电时 | 放电时 |
|--------|--------|--------|
| =maxsoc（满了） | 不能充，光伏全送网+弃 | — |
| =minsoc（没电了） | — | 不能放，储能不动 |

---

## 功率要平衡

```
光伏 = 送电网 + 充电 + 弃光
```

---

## 怎么输出？

```yaml
送电网: 10kW    # 电网送出
储能: 40kW      # 正=充电，负=放电
光伏充电: 40kW
光伏送网: 10kW
弃光: 0kW
原因: 充电+光伏>限值
```

---

## 例子直接看

| 场景 | 指令 | 光伏 | 限值 | 结果 |
|------|------|------|------|------|
| 充电，光伏多 | 100 | 50 | 10 | 充电40，送10 |
| 充电，光伏少 | 100 | 5 | 10 | 充电5，送0 |
| 待机，光伏多 | 0 | 50 | 10 | 充电40，送10 |
| 放电，光伏多 | -50 | 50 | 10 | 充电40，送10（反向） |
| 放电，光伏少 | -50 | 5 | 10 | 放电5，送5 |
| 充电，但已满 | 100 | 50 | 10 | 送10，弃40 |

---

## 充电桩（额外参考资料）

- 控制方式：功率 / 电流
- 车型判断：电流不平衡度≥10%是单相车
- 优先级：0-9，数字越小越优先
- 保护：三相不平衡时先削单相充电桩

---

name: egc-coordination-control

version: 1.0.0

Description: EGC Coordinated Control Logic Knowledge Base (FIP scenario)

category: domains

Tags: [EGC, FIP, microgrid, energy storage, photovoltaic]

allowed-tools: [Read, Write, Edit, Grep]

---

# EGC Coordinated Control (FIP)

# # # What is this?

FIP is a control strategy used to make a microgrid:

- Use photovoltaic power as much as possible and not waste it

- Don't buy electricity from the grid

- The excess electricity is either stored for energy or sent to the grid

---

# # Input parameters

| Parameters | What is it | Examples |

|------|--------|------|

| bess _ ap _ setpoint | AIM instructions (positive = charge, negative = discharge, 0 = regardless) | 100 / -50 / 0 |

| PV | How Much Electricity Does Photovoltaic Produce Now | 50kW |

| plant _ capacity | Total capacity | 100 kW |

| curtailment _ percent | curtailment percentage (%) | 10% |

| SOC | How much power is left in storage (%) | 50% |

# # # How does the limit be calculated?

```

Delivery limit value = site capacity x distribution limit ratio

Example: 100kW × 10% = 10kW

```

---

# 3 hard rules (the most important)

1.* * No electricity can be purchased from the grid * * Input limit = 0

2. * * Cannot be charged with electricity from the grid * * - Only charged with photovoltaics

3. * * Try to use photovoltaics * * * Don't waste

---

# # # How do I control it?

# # # charge instruction (bess _ ap _ setpoint > 0)

> Just let it store energy and charge

1. Photovoltaics charge energy storage first

2. The rest of the electricity goes to the grid (it cannot exceed the limit)

3. Just throw away as much as you want.

# # # standby instruction (bess _ ap _ setpoint = 0)

> Just keep it from moving

1. Photovoltaics are sent to the grid first

2. The rest charges the energy storage

3. Just throw away as much as you want.

# # # discharge command (bess _ ap _ setpoint < 0)

> Just let it discharge.

| Is PV enough or not | How to do it |

|----------|--------|

| PV ≥ limit value | Send to the grid full, energy storage does not discharge but is charged (reverse) |

| PV < limit value | All PV is sent to the grid, not enough discharge is needed to compensate |

---

# # Special Situations

| SOC State | When Charging | When Discharging |

|--------|--------|--------|

| = maxsoc (full) | can not be charged, photovoltaic full network + abandoned | - |

| = minsoc (out of power) | - | Can't put, energy storage does not move |

---

# # # Power must be balanced

```

PV = Grid Delivery + Charging + Discharge of Light

```

---

# # # How do I output?

```yaml

Power Supply: 10kW # Power Supply

Energy storage: 40kW # positive = charge, negative = discharge

Photovoltaic charging: 40kW

Photovoltaic network: 10 kW

Abandoned light: 0 kW

Cause: Charging + PV > Limit

```

---

# # # # Examples See directly

| Scenarios | Directives | PV | Limits | Results |

|------|------|------|------|------|

| Charge, PV Lot | 100 | 50 | 10 | Charge 40, send 10 |

| Charge, less PV | 100 | 5 | 10 | Charge 5 and send 0 |

| Standby, PV multiple | 0 | 50 | 10 | Charge 40, send 10 |

| Discharge, photovoltaic multi | -50 | 50 | 10 | Charge 40, send 10 (reverse) |

| Discharge, PV less | -50 | 5 | 10 | Discharge 5, send 5 |

| Charging, but full | 100 | 50 | 10 | Give 10, discard 40 |

---

## Charging stations (additional references)

- Control method: power / current

- Vehicle identification: If the current imbalance is ≥10%, it is a single-phase vehicle

- Priority: 0-9, the smaller the number, the higher the priority

- Protection: When the three-phase system is unbalanced, cut off the single-phase charging station first.