## premise (hidden)
premise
◆The accuracy of preventing reverse power flow shall be the detection level (whichever is greater, +5% of the rated output or +150W) and the detection time (within 5 minutes).
◆When output control is 0%
① In surplus power purchase, control is used to set the reverse power flow at the interconnection point to zero (self-consumption = power generation output, etc.), or to set the power generation output, etc. to 0%.
② In the case of full purchase, output control (0%) means that the power generation output etc. is set to 0%.
◆The time it takes for the output of the PCS, etc., to change from 100% to 0% output (0% to 100% output) can be adjusted in 1-minute increments within a 10-minute period.
(Error margin is ±5% (at room temperature)). The rate of change should be kept constant at "100%/(5-10 minutes)".

## Test List
| Kyushu Electric Power Co., Ltd. | Technical specifications for cases where a battery is installed alongside a renewable energy power source |  |  |  | 2025-10-21
Item No. | Technical Specifications | Items to be confirmed / Check point | Submitted data | Test method *1, *2 | Pass criteria | Remarks
1 | [Technical Specifications (1) and (3)] Assurance against the output control command value | If the reverse power flow from the power plant to the grid exceeds the output control command value, the renewable energy PCS and battery PCS will shut down within 5 minutes. | Data showing the interconnection point power, renewable energy generation power, and battery charging power relative to the output control command value at the time of deviation, for the cases of "renewable energy generation only" and "renewable energy generation + battery". | <Onamba> Send a 10% command to the pseudo power server. Send a 20% command to the pseudo power server. <Univers software support> ◆ Case: "Renewable generation only" *No need to stop the PCS on site ・Storage PCS in standby state (no charge/discharge command executed) ・Control rate 10% command -> turn OFF the control functions of the three PCS units (modify the point file) -> stop function enabled -> 5 minutes elapse -> PCS stops ・Control rate 20% command -> turn OFF the control functions of the three PCS units (modify the point file) -> stop function enabled -> 5 minutes elapse -> PCS stops ◆ Case: "Renewable generation + storage battery" *No need to stop the PCS on site ・Storage PCS in discharge state (Univers instruction: discharge 30% (450 kW)) ・Control rate 10% (150 kW) command -> turn OFF the control functions of the five PCS units (625 kW) (modify the point file) -> stop function enabled -> 5 minutes elapse -> PCS stops *It is sufficient if 1075 kW is output and the PCS and storage PCS stop ・Control rate 20% commandCommand -> Set the PCS control function for 5 units (625 kW) to OFF (revise the point file) -> stop function enabled -> after 5 minutes -> PCS stops ※ It is sufficient if 1,075 kW is output and the PCS and battery PCS stop. |  | When the 5-minute average is exceeded Execute the control command value on the emulator
② | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com |  |  | Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com | Upgrade for entire file translation at doc2lang.com |  | Upgrade for entire file translation at doc2lang.com
Upgrade for entire file translation at doc2lang.com

## summary
① Renewable energy
|  | Before starting | STEP 1 | STEP 2 | STEP 3 | STEP 4 | STEP 5
| Power server | 100% | 10% | 10% | 10% | 20% | 20%
| PV PCS | Power generation | Power generation | Stop | Power generation | Power generation | Stop
| Power storage PCS | charge/discharge | Stop or charge | Stop | Stop or charge | Stop or charge | Stop
| Electricity meter | Corresponding to solar radiation | Equivalent to 10% | 0kW | Equivalent to 10% | Equivalent to 20% | 0kW
| PCS control software | ― | ― | 1 unit control OFF | ― | ― | 1 unit control OFF
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.
① Renewable energy storage
|  | Before starting | STEP 1 | STEP 2 | STEP 3 | STEP 4 | STEP 5
| Power server | 100% | 10% | 10% | 10% | 20% | 20%
| PV PCS | Power generation | Power generation | Stop | Power generation | Power generation | Stop
| Power storage PCS | charge/discharge | Stop or charge | Stop | Stop or charge | Stop or charge | Stop
| Electricity meter | Corresponding to solar radiation | Equivalent to 10% | 0kW | Equivalent to 10% | Equivalent to 20% | 0kW
| PCS control software | ― | ― | 1 unit control OFF | ― | ― | 1 unit control OFF
| Aggregator | ― | 100% discharge | 100% discharge | 100% discharge | 100% discharge | 100% discharge
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.
② [Technical Specifications (2) (3)] <Optional for newly certified FIP and non-FIT from FY2024 onwards> Guarantee that battery charging power is derived from renewable energy.
|  | Before starting | STEP 1 | STEP 2 | STEP 2
| PV PCS | Power generation | Power generation | Stop | Stop
| Power storage PCS | charge/discharge | charge/discharge | Stop | Stop
| Electricity meter | Corresponding to solar radiation | Corresponding to solar radiation | 110kW charging | 110kW charging
| PCS control software | ― | Change settings | 100% charge | 1 unit control OFF
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.
③ 6.4 [Technical Specifications (4)] Responsiveness to Communication Anomalies
|  | Before starting | STEP 1 | STEP 2 | STEP 3 | STEP 4 | STEP 5 | STEP 6
| PV PCS | Power generation | Power generation | Power generation | Stop | Power generation | Stop | Power generation
| Power storage PCS | charging | charging | charging | Stop | charging | Stop | charging
| LAN router | connection | Lost track | connection | connection | connection | connection | connection
| LAN-PV PCS | connection | connection | connection | Lost track | connection | connection | connection
| LAN-Energy storage PCS | connection | connection | connection | connection | connection | Lost track | connection
| Electricity meter | Corresponding to solar radiation | Corresponding to solar radiation | Corresponding to solar radiation | 0kW | Corresponding to solar radiation | 0kW | Corresponding to solar radiation
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.
④ [Technical Specifications (1) (5)] Control accuracy relative to the control target value
|  | Before starting | STEP 1 | STEP 2 | STEP 3
| Power server | 100% | 10% | 30% | 60%
| PV PCS | Power generation | Power generation, suppression | Power generation, suppression | Power generation, suppression
| Power storage PCS | charge/discharge | charging | charging | charging
| Electricity meter | Corresponding to solar radiation | Equivalent to 10% | Equivalent to 30% | Equivalent to 60%
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.
⑤ [Technical Specifications (6)] Control Accuracy for Contracted Capacity Control
|  | Before starting | STEP 1 | STEP 2 | STEP 3 | STEP 4 | STEP 5
| Power server | 100% | 100% | 100% | 100% | 100% | 100%
| PV PCS | Power generation | Stop | Power generation | Stop | Stop | Start → Stop
| Power storage PCS | charging | Stop | charge/discharge | Stop | discharge 90% | Stop
| Electricity meter | Corresponding to solar radiation | 0kW | Corresponding to solar radiation | 0kW | Equivalent to 90% | 0kW
| Energy storage PCS control | ― | 100% discharge | Discharge instruction canceled | ― | discharge 90% | discharge 90%
Testing is required.
: Automatic state changes due to operation
: Numerical values, status, and items to check.

## ③ Communication
③ [Technical Specifications (4)] Responsiveness to Communication Anomalies
Exam on April 6th
Content | If a communication anomaly occurs between the PCS (in the broad sense) and the higher-level system, output control shall be implemented according to the latest output control schedule prior to the failure.
If an internal communication abnormality occurs in the PCS (in the broad sense), power generation and charging/discharging will be stopped for both renewable energy and battery storage.
Estimated test time: 1 hour
conditions | The battery must be capable of charging and discharging (guideline: around 50% SOC).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | ・Ten minutes before the shift change, disconnect the LAN cable between the power supply command and the output control unit (router ⇔ EMS HUB). | [5 empty] | STEP 1 | ① Disconnect the LAN cable from the router.
| Operate according to the saved output control schedule. (Basically 100%) | [6 empty] | Control will be performed at 20% of the total capacity (400kW).
STEP 2
| - Disconnect the LAN cable between the PVPCS and the output control unit (PV PCS ⇔ EMS HUB). | [5 empty] | STEP 3 | Disconnect the LAN cable between the smart logger and the EMS.
We confirmed that the PV PCS would shut down within 5 minutes using the PCS's functions.
STEP 4
| - Disconnect the LAN cable between the energy storage PCS and the output control unit (energy storage PCS ⇔ EMS HUB). | [5 empty] | STEP 5
We confirmed that the PCS (Power Conditioning System) would shut down within 5 minutes using its own functions.
STEP 6
Exam on April 7th
detail | No | Example time | Confirmation and operation details |  |  |  | STEP
|  |  | ONO |  | EPC, energy storage manufacturer | Univers
| 1 | 9:10 | The battery's SOC (State of Charge) is confirmed to be around 50%. The control will be set to 10% at the 9:30 frame. |  | The battery's SOC is confirmed to be around 50%. The control level will be set to 20%. | If the SOC is not within ±20% of 50%, issue a command to bring it closer to 50%. |  |  |  | MM | PCS1 | PCS2 | PCS3 | Power storage PCS1 | Power storage PCS2 | Power storage PCS3
| 2 | 9:20 | Disconnect the LAN cable between the power supply command and the output control unit (router-side LAN cable). | ✓ | 2026-03-02 | Disconnect the LAN cable between the power supply command and the output control unit (router-side LAN cable). | STEP 1 | 0:05 | 14:55 | 142 | 57 | 48 | 50
| 3 | 9:30 | Confirm that it operates according to the saved output control schedule (*1) | ✓ | 2026-03-02 |  |  | 0:15
| 4 | 9:40 | Set output control to 10%.
Exam on April 6th
| 1 | 14:00 | The battery's SOC is confirmed to be around 50%. Control will be set to 30% at 14:00. |  | The battery's SOC is confirmed to be around 50%. The control level will be set to 20%. | If the SOC is not within ±20% of 50%, issue a command to bring it closer to 50%. |  | 0:25
| 2 | 14:10 | Disconnect the LAN cable between the smart logger and the output control unit. Stop the PCS/power storage PCS. | ✓ | 2026-03-02 |  | STEP 2 | 0:30 | 14:45 | 251 | 82 | 86 | 87
| 6 | 14:20 | Confirm that the PV PCS will stop within 5 minutes. | ✓ | 2026-03-02 |  | STEP 3 | 0:35
| 6 | 14:51 | Confirm that the PV PCS will stop within 5 minutes. | ✓ | 2026-03-02 |  |  | 0:40
| 7 | 14:53 | Connect the LAN cable between the PV PCS and the output control unit, and confirm that the PV PCS starts up. | ✓ | 2026-03-02 |  | STEP 4 | 0:45 | [5 empty] | 9 | 9 | 9
| 8 | 9:46 | Disconnect the LAN cable between the energy storage PCS and the output control unit. | ✓ | 2026-03-03 |  | STEP 5 | 0:50 | [5 empty] | 0 | 0 | 0
| 9 | 9:51 | Confirm that the energy storage PCS will shut down within 5 minutes. | ✓ | 2026-03-03 |  |  | 0:55 | [5 empty] | 8.7 | 8.1 | 8.5
| 3 | 14:15 | Disconnect the LAN cable between the smart logger and the output control unit. Stop the PCS/power storage PCS. | ✓ | 2026-03-02 |  | STEP 2
| 3 | 14:16 | Connect the LAN cable between the energy storage PCS and the output control unit, and confirm that the energy storage PCS starts up. | ✓ | 2026-03-03 |  | STEP 6
|  | *1: | Check the values for grid connection point power, PV PCS, and energy storage PCS in DevPortal and AppPortal.
Check the reading on the power meter at the grid connection point and take a photograph.

## ④ Control
③ [Technical Specifications (1) (5)] Control accuracy relative to the control target value
Exam on April 6th
Content | The control error must be controllable to within ±5% of the rated output relative to the control target value.
Estimated test time: 1.5 hours
conditions | The battery must be capable of charging and discharging (guideline: around 50% SOC).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | Three control instructions were input from the simulated power server.
| - A 30% control instruction was input from the simulated power server. | [6 empty] | STEP 1
| - A 20% control instruction was input from the simulated power server. | [6 empty] | STEP 2
| - A 10% control instruction is input from the simulated power server. | [6 empty] | STEP 3
*The control rate is variable. Enter the control rate that allows you to see when control is applied based on the weather conditions.
detail | No | Example time | Confirmation and operation details |  |  |  |  | STEP
|  |  | ONO |  | EPC, energy storage manufacturer | Univers
| 1 | 14:30 | Battery State of Charge (SOC) confirmed to be around 50%. |  |  | If the SOC is not within ±20% of 50%, issue a command to bring it closer to 50%.
| 2 | 15:00 | Control instructions input from a simulated power server [14:30-14:59] [30%] | ✓ | 2026-03-04 |  |  | STEP 1 | 0:05
| 3 | 15:01 | Confirmed that 30% control has started. Confirmed that the power at the interconnection point has begun to decrease. | ✓ | 2026-03-04 |  |  |  | 0:15
| 4 | 15:10 | Confirmed that the power at the grid connection point is equivalent to 30% (*1) | ✓ | 2026-03-04 |  |  |  | 0:25
| 5 | 15:30 | Control instructions input from a simulated power server [15:30-15:59] [20%] | ✓ | 2026-03-04 |  |  | STEP 2 | 0:35
| 6 | 15:30 | Confirmed 20% control initiation. Confirmed that the power at the interconnection point has begun to decrease. | ✓ | 2026-03-04 |  |  |  | 0:45
| 7 | 15:31 | Confirmed that the power at the grid connection point is equivalent to 20% (*1) | ✓ | 2026-03-04 |  |  |  | 0:55
| 8 | 16:00 | Control instructions input from a simulated power server [16:00-16:29] [20%] | ✓ | 2026-03-04 |  |  | STEP 3 | 1:05
| 9 | 16:01 | Confirmed 10% control initiation. Confirmed that the power at the interconnection point has begun to decrease. | ✓ | 2026-03-04 |  |  |  | 1:15
| 10 | 16:10 | Confirmed that the power at the grid connection point is equivalent to 10% (*1) | ✓ | 2026-03-04 |  |  |  | 1:25
|  | *1: | Check the values for grid connection point power, PV PCS, and energy storage PCS in DevPortal and AppPortal.
Check the reading on the power meter at the grid connection point and take a photograph.

## ① Renewable energy
① [Technical Specifications (1) (3)] Guarantee against output control command values
◆ The case of "renewable energy generation only"
Content | If the reverse power flow from the power plant to the grid exceeds the output control command value,
The PV PCS and battery PCS must shut down within 5 minutes.
Estimated test time: 2 hours
conditions | The battery must be capable of charging and discharging (guideline: around 50% SOC).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | - A 10% control instruction is input from the simulated power server. |  |  |  |  | STEP 1
| The output control function of one PV PCS is turned OFF, creating a situation where the generated power deviates from the value indicated by the power server. (Univers software compatible) |  |  |  |  | STEP 2 | Since turning off the control function prevents stopping,
| Confirmed that the PV PCS and energy storage PCS would shut down within 5 minutes. | [5 empty] | The EGC command is set to 10%, but the software settings will be changed to run all three units at 100%.
STEP 3
| - A 20% control instruction was input from the simulated power server. |  |  |  |  | STEP 4
| The output control function of one PV PCS is turned OFF, creating a situation where the generated power deviates from the value indicated by the power server. (Univers software compatible) |  |  |  |  | STEP 5
Confirmed that the PV PCS and energy storage PCS would shut down within 5 minutes.
detail | No | Example time | Confirmation and operation details |  |  | STEP
|  |  | ONO | EPC, energy storage manufacturer | Univers
| 1 | 10:45 | Battery State of Charge (SOC) confirmed to be around 50%. |  | If the SOC is not within ±20% of 50%, issue a command to bring it closer to 50%.
| 2 | 13:40 | Control instructions input from a simulated power server [14:00-14:29] [5%] |  |  |  | 0:05
| 3 | 11:00 | Confirmed 10% control initiation. Confirmed that the power at the interconnection point has begun to decrease. |  |  | STEP 1 | 0:15
| 4 | 11:10 | Confirmed that the power at the grid connection point is equivalent to 10% (*1) |  |  |  | 0:25
| 5 | 11:15 |  |  | PCS1 output control reflection OFF | STEP 2 | 0:30
| 6 | 11:20 | Confirm that the PV PCS and energy storage PCS will shut down within 5 minutes. |  |  |  | 0:35
| 7 | 11:25 |  |  | Turn on the output control function of PCS1. |  | 0:40
| 8 | 11:30 |  | PV PCS and energy storage PCS are started. |  | STEP 3 | 0:45
| 9 | 11:30 | Confirmed startup of PV PCS and energy storage PCS. |  |  |  | 0:45
| 10 | 11:50 | Control instructions input from a simulated power server [12:00-12:29] [20%] |  |  |  | 1:05
| 11 | 12:00 | Confirmed 10% control initiation. Confirmed that the power at the interconnection point has begun to decrease. |  |  | STEP 4 | 1:15
| 12 | 12:10 | Confirmed that the power at the grid connection point is equivalent to 20% (*1) |  |  |  | 1:25
| 13 | 12:15 |  |  | PCS1 output control reflection OFF | STEP 5 | 1:30
| 14 | 12:20 | Confirm that the PV PCS and energy storage PCS will shut down within 5 minutes. |  |  |  | 1:35
| 15 | 12:25 |  |  | Turn on the output control function of PCS1. |  | 1:40
| 16 | 12:30 |  | PV PCS and energy storage PCS are started. |  |  | 1:45
| 17 | 12:30 | Confirmed startup of PV PCS and energy storage PCS. |  |  |  | 1:45
|  | *1: | Check the values for grid connection point power, PV PCS, and energy storage PCS in DevPortal and AppPortal.
Check the reading on the interconnection point meter and take a photo.

## ① Renewable energy storage
① [Technical Specifications (1) (3)] Guarantee against output control command values
◆ The case of "renewable energy generation + battery storage"
Content | If the reverse power flow from the power plant to the grid exceeds the output control command value,
The PV PCS and battery PCS must be shut down within 5 minutes.
| *If both a power server instruction and an aggregator instruction are received simultaneously, the power server instruction takes precedence. |  |  |  | Estimated test time: 2 hours
conditions | The battery must be capable of charging and discharging (guideline: around 50% SOC).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | - A discharge command (100% discharge instruction) simulating an aggregator command is sent from the cloud. (Univers) |  |  |  |  | STEP 1
| - A 10% control instruction is input from the simulated power server. |  |  |  |  | STEP 2
The output control function of one PV PCS is turned OFF, creating a situation where the generated power deviates from the value indicated by the power server. (Univers software compatible)
Confirmed that the PV PCS and energy storage PCS would shut down within 5 minutes.
STEP 3
| - A 20% control instruction was input from the simulated power server. |  |  |  |  | STEP 4
| The output control function of one PV PCS is turned OFF, creating a situation where the generated power deviates from the value indicated by the power server. (Univers software compatible) |  |  |  |  | STEP 5
Confirmed that the PV PCS and energy storage PCS would shut down within 5 minutes.
detail | No | Example time | Confirmation and operation details |  |  | STEP
|  |  | ONO | EPC, energy storage manufacturer | Univers
| 1 | 12:45 | Battery State of Charge (SOC) confirmed to be around 50%. |  | If the SOC is not within ±20% of 50%, issue a command to bring it closer to 50%.
| 2 | 12:50 | Control instructions input from a simulated power server [13:00-13:29] [10%] |  | Sending a pseudo-aggregator command [100% discharge] |  | 0:05
| 3 | 13:00 | Confirmed 10% control initiation. Confirmed that the power at the interconnection point has begun to decrease. |  |  | STEP 1 | 0:15
| 4 | 13:10 | Confirmed that the power at the grid connection point is equivalent to 10% (*1) |  |  |  | 0:25
| 5 | 13:15 |  |  | PCS1 output control reflection OFF | STEP 2 | 0:30
| 6 | 13:20 | Confirm that the PV PCS and energy storage PCS will shut down within 5 minutes. |  |  |  | 0:35
| 7 | 13:25 |  |  | Turn on the output control function of PCS1. |  | 0:40
| 8 | 13:30 |  | PV PCS and energy storage PCS are started. |  | STEP 3 | 0:45
| 9 | 13:30 | Confirmed startup of PV PCS and energy storage PCS. |  |  |  | 0:45
| 10 | 13:50 | Control instructions input from a simulated power server [14:00-14:29] [20%] |  |  |  | 1:05
| 11 | 14:00 | Confirmed 10% control initiation. Confirmed that the power at the interconnection point has begun to decrease. |  |  | STEP 4 | 1:15
| 12 | 14:10 | Confirmed that the power at the grid connection point is equivalent to 20% (*1) |  |  |  | 1:25
| 13 | 14:15 |  |  | PCS1 output control reflection OFF | STEP 5 | 1:30
| 14 | 14:20 | Confirm that the PV PCS and energy storage PCS will shut down within 5 minutes. |  |  |  | 1:35
| 15 | 14:25 |  |  | Turn on the output control function of PCS1. |  | 1:40
| 16 | 14:30 |  | PV PCS and energy storage PCS are started. |  |  | 1:45
| 17 | 14:30 | Confirmed startup of PV PCS and energy storage PCS. |  | Deactivate the pseudo-aggregator command. |  | 1:45
|  | *1: | Check the values for grid connection point power, PV PCS, and energy storage PCS in DevPortal and AppPortal.
Check the reading on the interconnection point meter and take a photo.

## ② Grid charging
① [Technical Specifications (2) (3)] <Optional for newly certified FIP and non-FIT from FY2024 onwards> Guarantee that battery charging power is derived from renewable energy.
Content | (2) If the power generated by renewable energy exceeds the power charged by the battery, the PCS for renewable energy and the PCS for battery storage will shut down within 5 minutes.
If forward power flow (grid → power generation equipment) is detected at the interconnection point while the battery is charging, the renewable energy PCS and the battery PCS will shut down within 5 minutes.
Estimated test time: 0.5 hours
conditions | The battery must be rechargeable (guideline: SOC 70% or less).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | A manual 100% charge command is sent to Univers EMS to achieve the battery's charged state. |  |  |  |  | STEP 1
The power meter reading is adjusted to reflect electricity sold from the grid (by shifting more than 5% of the rated output towards charging).
| We confirmed that when the power generated by the PV PCS exceeds the power charged by the energy storage PCS, both the PV PCS and the energy storage PCS will shut down within 5 minutes. |  |  |  |  | STEP 2
75
detail | No | Example time | Confirmation and operation details |  |  | STEP
|  |  | ONO | EPC, energy storage manufacturer | Univers
| 1 | 12:45 | Check that the battery's State of Charge (SOC) is below 70%. |  | Discharge command input when SOC is 70% or higher.
| 2 | 12:50 |  |  | Change the meter reading setting | STEP 1 | 0:05
| 2 | 12:50 |  |  | Send a 100% charge command to the EMS from the cloud environment. | STEP 1 | 0:05
| 3 | 12:55 | Confirm that the PV PCS and energy storage PCS will shut down within 5 minutes. |  |  | STEP 2 | 0:10
| 4 | 13:00 |  |  | Cancel the charging command from the cloud environment. | STEP 3 | 0:15
| 4 | 13:05 |  |  | Reset meter reading settings to operational state | STEP 3 | 0:20
| 5 | 13:10 | Confirmed startup of PV PCS and energy storage PCS. |  |  | STEP 4 | 0:25
6
7
8
9
10

## ⑤ RPR
⑤ [Technical Specifications (6)] Control Accuracy for Contracted Capacity Control
Content | If the reverse power flow from the power plant to the grid exceeds the contracted capacity,
| To stop or suppress PV PCS and energy storage PCS with accuracy equivalent to RPR. | [5 empty] | Accuracy equivalent to RPR (0.5–2.0 seconds)
Estimated test time: 1 hour
conditions | The battery must be able to discharge (guideline: SOC 30% or higher).
The PV PCS must be in a state where it can generate electricity (during the daytime).
overview | ・EMSBattery manufacturersSet the instruction to force a 100% discharge. |  |  |  |  | STEP 1
*If this is not possible, set the 100% discharge command from Univers.
- Confirmed that the PV PCS power generation power + battery discharge power exceeded the rated value, causing the PV PCS and battery PCS to shut down with accuracy equivalent to RPR.
STEP 2
| - Stop all PV PCS units. |  |  |  |  | STEP 3
| - The battery manufacturer will set a forced 90% discharge instruction. |  |  |  |  | STEP 4
| Start PV PCS. |  |  |  |  | STEP 5
It was confirmed that the PV PCS power generation power + battery discharge power exceeded the rated value, causing the PV PCS and battery PCS to shut down with accuracy equivalent to RPR.
detail | No | Example time | Confirmation and operation details |  |  | STEP
|  |  | ONO | EPC, energy storage manufacturer | Univers
| 1 | 12:50 | Confirm that the battery's State of Charge (SOC) is 30% or higher. |  | When SOC is below 30%, input charging command.
| 2 | 12:55 |  | Set the command to 100% forced discharge. | If the battery manufacturer cannot provide support, set the instruction to 100% discharge. | STEP 1 | 0:05
| 3 | 12:55 | Confirmed that the PV PCS and energy storage PCS have stopped down (*1) |  |  |  | 0:05
| 4 | 13:00 |  | Cancel the forced discharge instruction. | If a discharge command is issued in No. 2, the discharge command will be canceled. | STEP 2 | 0:10
| 5 | 13:05 | Confirmed startup of PV PCS and energy storage PCS. |  |  |  | 0:15
| 6 | 13:15 |  | All PV PCS units have been shut down. |  | STEP 3 | 0:25
| 7 | 13:20 |  | Set the command to force discharge to 90%. | If the battery manufacturer cannot provide support, set the discharge instruction to 90%. | STEP 4 | 0:30
| 8 | 13:25 |  | Start PV PCS |  | STEP 5 | 0:35
| 9 | 13:25 | Confirmed that the PV PCS and energy storage PCS have stopped down (*1) |  |  |  | 0:35
| 10 | 13:30 |  | Cancel the forced discharge instruction. | If a discharge command is issued in No. 7, the discharge command will be canceled. |  | 0:40
Check with an oscilloscope.
|  | *1: | Check the values for grid connection point power, PV PCS, and energy storage PCS in DevPortal and AppPortal.
Check the reading on the interconnection point meter and take a photo.