## New Function configuration
Configuration file path: /root/EMS/edge-ems/resources/microgridcontroller/microgridcontroller.config
Function | New configuration item | Configuration Parameter Explanation | Default value | screenshot
fail safe logic of dynamic exportlimit exceed | Dynamic Export Limit Protection Switch | Through HMI configuration,"Site Overcapactiy Protection" Support configuration of fixed values or dynamic judgment. Configuring as "Fixed Value" indicates disabling the dynamic overcapacity prevention function and using the configured value for judgment. Configuring as "Measurement Point" indicates enabling the dynamic overcapacity prevention function. | --
| dynamicGridExportLimitMargin | By modifying through the configuration file，The default value is 0. | 0
| EssChargeForImportLimitationSwitch | The modification is made through the configuration file, with the default value being 0. For FIP sites, it needs to be set to 1. | 0

## Control strategy configuration
Control strategy configuration： （The unspecified configuration is "Disabled"） | Add the following configuration to the configuration file： | comment
- Current control strategy：Power Curtailment - Power Curtailment：Enabled； - Site export capacity： 1500kW - Output control time： 60s - Static Demand Management ：Enabled - Maximum Import Power： 0kW- Demand Response：Enabled - Control Cycle：1s - Power Sign：Positive Consumption, Negative Generation - Maximize Local PV Consumption：Enabled - Grid Charge BESS：Enabled - Site Overcapactiy Protection：Enabled - Site Overcapactiy Protection triggering condition： - Import limit ：99kW； - Export limit ：dynamic； - Duration Period：0 | failsafeEssStopEnable=1 essStopValue=1 pvStopValue=1 failsafeSendStopTimes=1 dynamicGridExportLimitMargin=99 EssChargeForImportLimitationSwitch=1 | Some test cases will modify the configuration.Different configurations will be described in the "precondition" or "Test step" columns.

## Functtion Test result
No | Test-item | precondition | Test step | Pass standard | result
1 | RPR-Equivalent Control Test-Normal Scenario | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | Initial State: Curtailment ratio = 100 % ap_export_upper_limit=1500kW bess_ap_setpoint = -1500kW =================== BS.ActivePW=-1500 kW (discharge) METER.ActivePW=-1500kW PV not active SoC=50% =================== Operation: - At the 4th minute, change PV status to controllable with power output of 500 kW - The first four minutes: Meter power = -1500kW（BESS Power 1500）；After the fourth minute Meter power = -1500kW（INV Power 1500kW） | EGC reduces BESS power, controls output limit not to exceed Limit =========EGC output========== INV.LimitPower=500kW*3 units BS.SysAPSetPoint=0kW*3 units | pass
2 | RPR-Equivalent Control Test-Abnormal Protection Triggered | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | Initial State: Curtailment ratio = 100 % ap_export_upper_limit=1500kW bess_ap_setpoint = -1500kW =================== BS.ActivePW=-1500 kW (discharge) METER.ActivePW=-1500kW PV not active SoC=50% =================== Operation: - At the 4th minute, change PV status to controllable with power output of 500 kW, and device does not follow control - The first four minutes: Meter power = -1500kW（BESS Power 1500）；After the fourth minute Meter power = -3000kW（BESS Power 1500kW+ INV Power 1500kW） | Device does not follow control, algorithm enters abnormal protection； PV and BESS be stopped (INV.Stop, BS.Stop). =========EGC output========== INV.LimitPower=0kW*3 units BS.SysAPSetPoint=0kW*3 units INV.Stop=1*3 units BS.Stop=1*3 units | pass
3 | BESS + PV Curtailment Test-Normal Scenario | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | Initial State: Curtailment ratio = 100 % ap_export_upper_limit=1500kW bess_ap_setpoint = -1500kW dynamicGridExportLimitMargin = 75kW Output control time = 10s =================== BS.ActivePW=-60 kW*3 INV.GenActivePW=60kW*3 METER.ActivePW=-360kW SoC=50% =================== Operation Steps: - Modify curtailment limit = 20%, PV and BESS do not follow, maintain power as: BS.ActivePW=-60 kW*3 INV.GenActivePW=60kW*3 - Curtailment ratio = 20 % - ap_export_upper_limit=300kW - Meter power = -360kW | PV = 60 kW × 3 BESS = -60 kW × 3 export > limit 360 - 300 = 60, margin = 75, not exceeding margin, will not trigger abnormal protection =========EGC output========== INV.LimitPower=85kW*3 units BS.SysAPSetPoint=15kW*3 units | pass
4 | BESS + PV Curtailment Test-Abnormal Protection Triggered | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | Initial State: Curtailment ratio = 100 % ap_export_upper_limit=1500kW bess_ap_setpoint = -1500kW dynamicGridExportLimitMargin = 75kW Output control time = 10s =================== BS.ActivePW=-100 kW*3 INV.GenActivePW=100kW*3 METER.ActivePW=-60kW SoC=50% =================== Operation Steps: - Modify curtailment limit = 20%, PV and BESS do not follow, maintain power as: BS.ActivePW=-100 kW*3 INV.GenActivePW=100kW*3 - Curtailment ratio = 20 % - ap_export_upper_limit=300kW - Meter power = -600kW | PV and BESS devices do not follow control, exceeding output limit triggers abnormal protection PV = 100 × 3 BESS = 100 × 3 export > limit 600 > 300 PV and BESS be stopped (INV.Stop, BS.Stop). =========EGC output========== INV.LimitPower=0kW*3 units BS.SysAPSetPoint=0kW*3 units INV.Stop=1*3 units BS.Stop=1*3 units | pass
6 | PV Curtailment Test-Abnormal Protection Triggered | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | Initial State: Curtailment ratio = 100 % ap_export_upper_limit=1500kW bess_ap_setpoint = 0kW dynamicGridExportLimitMargin = 75kW Output control time = 10s =================== BS.ActivePW= 0 kW*3 INV.GenActivePW= 200kW*3 METER.ActivePW=-600kW SoC=50% =================== - Curtailment limit = 10%, PV and BESS do not follow, maintain power as: BS.ActivePW= 0 kW*3 INV.GenActivePW= 200kW*3 - Curtailment ratio = 10 % - ap_export_upper_limit=150kW - Meter power = -600kW | PV device does not follow control, exceeding output limit triggers abnormal protection PV = 200 × 3 BESS = 0 × 3 export > limit 600-150=450 450 > 75 PV and BESS be stopped (INV.Stop, BS.Stop). =========EGC output========== INV.LimitPower=0kW*3 units BS.SysAPSetPoint=0kW*3 units INV.Stop=1*3 units BS.Stop=1*3 units | pass
7 | Output Accuracy Control | Equipment Configuration: - PV: 500 kW × 3 units - BESS: 500 kW × 3 units | bess_ap_setpoint = 0 kW - Curtailment limit = 100%, ap_export_upper_limit=1500kW PV is active BESS is active observe phenomenon | EGC controls site output power to 1500 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 0 × 3 | pass
8 |  |  | bess_ap_setpoint = 0 kW - Curtailment limit = 60%, ap_export_upper_limit=900kW PV is active BESS is active observe phenomenon | EGC controls site output power to 900 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 200 × 3 | pass
9 |  |  | bess_ap_setpoint = 0 kW - Curtailment limit = 10%, ap_export_upper_limit=150kW PV is active BESS is active observe phenomenon | EGC controls site output power to 150 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 450 × 3 | pass
10 | EGC Coordination Logic-Charge setpoint-curtailment is 0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW | pass
11 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW | pass
12 | EGC Coordination Logic-Charge setpoint-curtailment is 50% |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
13 |  |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=50kW | pass
14 | EGC Coordination Logic-Charge setpoint-curtailment is 100% |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
15 |  |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge = ¦Ppvload¦； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=50kW | pass
16 | EGC Coordination Logic-Charge setpoint-SoC = Max SoC |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=100% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0kW | pass
17 |  |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=100% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=999.5kW BS.SysAPSetPoint=0kW | pass
18 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=100% =================== bess_ap_setpoint=1000kW | SoC = Max SoC； =========EGC output========== INV.LimitPower=0kW BS.SysAPSetPoint=0kW | pass
19 | EGC Coordination Logic-DisCharge setpoint-curtailment is 0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW | pass
20 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW | pass
21 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW | pass
22 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW | pass
23 | EGC Coordination Logic-DisCharge setpoint-curtailment is 50% |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
24 |  |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=0kW | pass
25 |  |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=999.5kW BS.ActivePW=0kW METER.ActivePW=-999.5kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV > export limit ； ESS Charge= INV-export limit； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0.5kW | pass
26 |  |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=100kW BS.ActivePW=0kW METER.ActivePW=-100kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV + Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=150kW BS.SysAPSetPoint=-849.5kW | pass
27 | EGC Coordination Logic-DisCharge setpoint-curtailment is 10% |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
28 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=200kW BS.ActivePW=0kW METER.ActivePW=-200kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV > export limit ； ESS Charge= INV-export limit； INV.LimitPower=250kW BS.SysAPSetPoint=50.1kW | pass
29 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-149.9kW | pass
30 | EGC Coordination Logic-DisCharge setpoint-curtailment is 100% |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
31 |  |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0kW | pass
32 |  |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=-999kW | pass
33 | EGC Coordination Logic- bess_ap_setpoint is 0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW | pass
34 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW | pass
35 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=199,9kW BS.ActivePW=0kW METER.ActivePW=-199,9kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=249.9kW BS.SysAPSetPoint=50kW | pass
36 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=199,9kW BS.ActivePW=0kW METER.ActivePW=-199,9kW SoC=100% =================== bess_ap_setpoint=0kW | =========EGC output========== INV.LimitPower=199.9kW BS.SysAPSetPoint=0kW | pass
37 | EGC Coordination Logic- bess_ap_setpoint = 0 ; load >0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW | pass
38 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW | pass
39 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW | pass
40 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=50kW BS.ActivePW=-10kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；Reduce ESS =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=40kW | pass
41 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=100kW BS.ActivePW=40kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=150kW BS.SysAPSetPoint=90kW | pass
42 | EGC Coordination Logic- bess_ap_setpoint < 0 ; load >0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW | pass
43 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW | pass
44 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-159.9kW | pass
45 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=150kW BS.ActivePW=-59.9kW METER.ActivePW=-199.9kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；Reduce ESS =========EGC output========== INV.LimitPower=200kW BS.SysAPSetPoint=-9.9kW | pass
46 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=200kW BS.ActivePW=-9.9kW METER.ActivePW=-199.9kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up ,ESS Charge =========EGC output========== INV.LimitPower=250kW BS.SysAPSetPoint=40.1kW | pass
47 | EGC Coordination Logic- bess_ap_setpoint >0 ; load >0 | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW | pass
48 |  |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW | pass
49 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW | pass
50 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=50kW BS.ActivePW=-10kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=40kW | pass
51 |  |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=1000kW BS.ActivePW=940kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=990kW | pass
52 | EGC Coordination Logic-Charge setpoint-SoC = Max SoC | Equipment Configuration: - PV: 1000 kW × 1 units - BESS: 1000 kW × 1 units Site export capacity： 1999kW | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=1000kW BS.ActivePW=1000kW METER.ActivePW=0kW SoC=100% =================== bess_ap_setpoint=1000kW | SoC = Max SoC； =========EGC output========== INV.LimitPower=0kW BS.SysAPSetPoint=0kW
53 | 5‑minute average grid meter import power > import limit |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - Site Overcapactiy Protection：Enabled - Site Overcapactiy Protection triggering condition： - Import limit ：99kW； - Export limit ：dynamic； =================== INV.GenActivePW=50kW BS.ActivePW=150kW METER.ActivePW=100kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | import power= 100; Import limit=99kW； 100 > 99 ,so algorithm enters abnormal protection； =========EGC output========== INV.LimitPower=0kW*3 units BS.SysAPSetPoint=0kW*3 units INV.Stop=1*3 units BS.Stop=1*3 units
54 | 5‑minute average grid meter import power < import limit |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW Grid import limit =0kW - Site Overcapactiy Protection：Enabled - Site Overcapactiy Protection triggering condition： - Import limit ：99kW； - Export limit ：dynamic； =================== INV.GenActivePW=50kW BS.ActivePW=80kW METER.ActivePW=30kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | import power= 30; Import limit=99kW； 30 < 99 ,so algorithm will not enter the exception protection.
55 | 5‑minute average grid meter import power = import limit |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - Site Overcapactiy Protection：Enabled - Site Overcapactiy Protection triggering condition： - Import limit ：99kW； - Export limit ：dynamic；- =================== INV.GenActivePW=50kW BS.ActivePW=149kW METER.ActivePW=99kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | import power= 99; Import limit=99kW； 99 = 99 ,so algorithm will not enter the exception protection.

## Test screenshot
No | Test-item | Test step | Pass standard | Screenshot
1 | RPR-Equivalent Control Test-Normal Scenario | Initial State: - Curtailment limit = 100% - bess_ap_setpoint = -1500 - BESS Power = -1500 kW (discharge) - PV not active Operation: - At the 4th minute, change PV status to controllable with power output of 500 kW | EGC reduces BESS power, controls output limit not to exceed Limit PV = 500 × 3 BESS = 0 × 3
2 | RPR-Equivalent Control Test-Abnormal Protection Triggered | Initial State: - Curtailment limit = 100% - bess_ap_setpoint = -1500 - BESS at full discharge = -1500 kW - PV not controllable Operation: - At the 4th minute, change PV status to controllable with power output of 500 kW, and device does not follow control | Device does not follow control, algorithm enters abnormal protection； PV and BESS be stopped (INV.Stop, BS.Stop).
3 | BESS + PV Curtailment Test-Normal Scenario | Initial State: - Curtailment limit = 100% - bess_ap_setpoint = -1500 - dynamicGridExportLimitMargin = 75 - Control cycle = 1s - Curtailment regulation time = 10s Operation Steps: - Modify curtailment limit = 20%, PV and BESS do not follow, maintain power as: PV = 60 kW × 3 BESS = -60 kW × 3 | PV = 60 kW × 3 BESS = -60 kW × 3 export > limit 360 - 300 = 60, margin = 75, not exceeding margin, will not trigger abnormal protection
4 | BESS + PV Curtailment Test-Abnormal Protection Triggered | Initial State: - Curtailment limit = 100% - bess_ap_setpoint = -1500 - dynamicGridExportLimitMargin = 75 - Control cycle = 1s - Curtailment regulation time = 10s Operation Steps: - Modify curtailment limit = 20%, PV and BESS do not follow, maintain power as: PV = 100 kW × 3 BESS = -100 kW × 3 | PV and BESS devices do not follow control, exceeding output limit triggers abnormal protection PV = 100 × 3 BESS = 100 × 3 export > limit 600 > 300 PV and BESS be stopped (INV.Stop, BS.Stop).
6 | PV Curtailment Test-Abnormal Protection Triggered | bess_ap_setpoint = 0 kW - Curtailment limit = 10%, PV and BESS do not follow, maintain power as: PV = 200 kW × 3 BESS = 0 kW × 3 | PV device does not follow control, exceeding output limit triggers abnormal protection PV = 200 × 3 BESS = 0 × 3 export > limit 600 > 150 PV and BESS be stopped (INV.Stop, BS.Stop).
7 | Output Accuracy Control | bess_ap_setpoint = 0 kW - Curtailment limit = 100%, observe phenomenon | EGC controls site output power to 1500 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 0 × 3
8 |  | bess_ap_setpoint = 0 kW - Curtailment limit = 60%, observe phenomenon | EGC controls site output power to 900 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 200 × 3
9 |  | bess_ap_setpoint = 0 kW - Curtailment limit = 10%, observe phenomenon | EGC controls site output power to 150 kW, will not exceed output limit to trigger abnormal protection PV = 500 × 3 BESS = 450 × 3
10 | EGC Coordination Logic-Charge setpoint-curtailment is 0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW
11 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW
12 | EGC Coordination Logic-Charge setpoint-curtailment is 50% | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
13 |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=50kW
14 | EGC Coordination Logic-Charge setpoint-curtailment is 100% | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
15 |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge = ¦Ppvload¦； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=50kW
16 | EGC Coordination Logic-Charge setpoint-SoC = Max SoC | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=100% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0kW
17 |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=100% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=999.5kW BS.SysAPSetPoint=0kW
18 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=100% =================== bess_ap_setpoint=1000kW | SoC = Max SoC； =========EGC output========== INV.LimitPower=0kW BS.SysAPSetPoint=0kW
19 | EGC Coordination Logic-DisCharge setpoint-curtailment is 0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW
20 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW
21 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW
22 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=50kW BS.ActivePW=50kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS + INV Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=100kW
23 | EGC Coordination Logic-DisCharge setpoint-curtailment is 50% | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
24 |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=50kW BS.ActivePW=0kW METER.ActivePW=-50kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=0kW
25 |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=999.5kW BS.ActivePW=0kW METER.ActivePW=-999.5kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV > export limit ； ESS Charge= INV-export limit； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0.5kW
26 |  | Curtailment ratio = 50 % ap_export_upper_limit=999.5kW - =================== INV.GenActivePW=100kW BS.ActivePW=0kW METER.ActivePW=-100kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV + Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=150kW BS.SysAPSetPoint=-849.5kW
27 | EGC Coordination Logic-DisCharge setpoint-curtailment is 10% | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
28 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=200kW BS.ActivePW=0kW METER.ActivePW=-200kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV > export limit ； ESS Charge= INV-export limit； INV.LimitPower=250kW BS.SysAPSetPoint=50.1kW
29 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-149.9kW
30 | EGC Coordination Logic-DisCharge setpoint-curtailment is 100% | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
31 |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=0% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=0kW
32 |  | Curtailment ratio = 100 % ap_export_upper_limit=1999kW - =================== INV.GenActivePW=1000kW BS.ActivePW=0kW METER.ActivePW=-1000kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS DisCharge； INV + ESS = export_upper_limit =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=-999kW
33 | EGC Coordination Logic- bess_ap_setpoint is 0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=50kW
34 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=0kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=0kW
35 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=199,9kW BS.ActivePW=0kW METER.ActivePW=-199,9kW SoC=0% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS + Ramp up =========EGC output========== INV.LimitPower=249.9kW BS.SysAPSetPoint=50kW
36 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=199,9kW BS.ActivePW=0kW METER.ActivePW=-199,9kW SoC=100% =================== bess_ap_setpoint=0kW | =========EGC output========== INV.LimitPower=199.9kW BS.SysAPSetPoint=0kW
37 | EGC Coordination Logic- bess_ap_setpoint = 0 ; load >0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW
38 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW
39 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW
40 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=50kW BS.ActivePW=-10kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up；Reduce ESS =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=40kW
41 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=100kW BS.ActivePW=40kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=0kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=150kW BS.SysAPSetPoint=90kW
42 | EGC Coordination Logic- bess_ap_setpoint < 0 ; load >0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW
43 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW
44 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-159.9kW
45 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=150kW BS.ActivePW=-59.9kW METER.ActivePW=-199.9kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up；Reduce ESS =========EGC output========== INV.LimitPower=200kW BS.SysAPSetPoint=-9.9kW
46 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=200kW BS.ActivePW=-9.9kW METER.ActivePW=-199.9kW load =10kW SoC=50% =================== bess_ap_setpoint=-1000kW | INV+ Ramp up ,ESS Charge =========EGC output========== INV.LimitPower=250kW BS.SysAPSetPoint=40.1kW
47 | EGC Coordination Logic- bess_ap_setpoint >0 ; load >0 | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； =========EGC output========== INV.LimitPower=10kW BS.SysAPSetPoint=0kW
48 |  | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=60kW load =60kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW
49 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=0kW BS.ActivePW=0kW METER.ActivePW=10kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up；ESS Discharge =========EGC output========== INV.LimitPower=50kW BS.SysAPSetPoint=-10kW
50 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=50kW BS.ActivePW=-10kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=100kW BS.SysAPSetPoint=40kW
51 |  | Curtailment ratio = 10 % ap_export_upper_limit=199.9kW - =================== INV.GenActivePW=1000kW BS.ActivePW=940kW METER.ActivePW=-50kW load =10kW SoC=50% =================== bess_ap_setpoint=1000kW | INV+ Ramp up； ESS Charge =========EGC output========== INV.LimitPower=1000kW BS.SysAPSetPoint=990kW
52 | EGC Coordination Logic-Charge setpoint-SoC = Max SoC | Curtailment ratio = 0 % ap_export_upper_limit=0kW - =================== INV.GenActivePW=1000kW BS.ActivePW=1000kW METER.ActivePW=0kW SoC=100% =================== bess_ap_setpoint=1000kW | SoC = Max SoC； =========EGC output========== INV.LimitPower=0kW BS.SysAPSetPoint=0kW
53 | 5‑minute average grid meter import power > import limit | Curtailment ratio = 0 % ap_export_upper_limit=0kW Grid import limit =0kW The input limit values used to trigger the abnormal protection against over-capacity in the station field = 99kW - =================== INV.GenActivePW=50kW BS.ActivePW=150kW METER.ActivePW=100kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | algorithm enters abnormal protection； PV and BESS be stopped (INV.Stop, BS.Stop,and INV.LimitPower=0kW,BS.SysAPSetPoint=0kW).
54 | 5‑minute average grid meter import power < import limit | Curtailment ratio = 0 % ap_export_upper_limit=0kW Grid import limit =0kW The input limit values used to trigger the abnormal protection against over-capacity in the station field = 99kW - =================== INV.GenActivePW=50kW BS.ActivePW=80kW METER.ActivePW=30kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | algorithm will not enter the exception protection.
55 | 5‑minute average grid meter import power = import limit | Curtailment ratio = 0 % ap_export_upper_limit=0kW Grid import limit =0kW The input limit values used to trigger the abnormal protection against over-capacity in the station field = 99kW - =================== INV.GenActivePW=50kW BS.ActivePW=149kW METER.ActivePW=99kW SoC=50% -Continue for five minutes and keep the "activepw" unchanged. =================== | algorithm will not enter the exception protection.