UNIVERS CO., LTD.

EGC & FCR Local Protection Rule Book

| Document ID | UNIV-EGC-PROT-001 |
| --- | --- |
| Version | 0.2 (Updated with PRD Review Inputs) |
| Date | April 2026 |
| Status | AIM internal review, then dev & QA reinput |
| Author | Frankie, Jiahui, Zhengkhoon |
| Contributors | Yintao, Xuezheng, Yasuoka Mitsuaki, Shogo Moroishi, Kazu Yurita, Suk Lee |

Change Log

| Version | Date | Change |
| --- | --- | --- |
| 0.1 | Feb 2026 | Initial framework based on Nogi RCA and rule book email |
| 0.2 | Feb 2026 | Updated with EGC PRD review inputs (EGC4001, EGC4006, FIP protections); added FIP/hybrid section; added missing edge-case scenarios |
| 0.3 |  |  |

# 1. Purpose and Scope

This document defines the expected behavior of the EGC, FCR Controller, and Enflex Adaptor under normal, degraded, and failure conditions. It serves three audiences:

| Audience | Use Case |
| --- | --- |
| O&M / L2 Support | Diagnose site behavior, answer “why did it do that?” |
| Aggregators & Customers | Understand fail-safe guarantees when handing control to Univers EMS |
| Dev / QA | Validate logic against defined rules; regression-test edge cases |

## 1.1 Motivation

The Nogi FCR Issue No.3 (November 2025) demonstrated that undocumented protection mechanisms — combined with configuration errors — can cascade into severe operational incidents (2000 kW oscillation). Without a single reference describing each protection rule, its trigger, its effect, and its interactions with other rules, we cannot reliably support, debug, or scale.

## 1.2 Component Scope

| Component | Abbreviation | Role |
| --- | --- | --- |
| Edge Grid Controller | EGC | Site-level optimisation, dispatch, protection logic |
| FCR Controller | FCR-C | Frequency containment reserve response (droop-based) |
| Enflex Adaptor | Adaptor | Cloud ↔ site bridge; aggregator command relay |
| BESS Controller / PCS | PCS | Southbound device executing kW commands |
| PV PCS | PV-PCS | PV inverter (relevant for FIP hybrid sites) |

## 1.3 Site Topology Applicability

Each scenario card indicates which site topologies it applies to, since behavior differs significantly:

| Topology | Description | Key Differences |
| --- | --- | --- |
| BESS Standalone | BESS only, no co-located generation | Simplest load calculation; FCR or arbitrage |
| FIP (PV + BESS) | AC-coupled PV + BESS under FIP scheme | Reverse power flow protection; renewable-only charging; PV curtailment interactions |
| DC-Coupled Hybrid | PV DC-coupled to BESS | Much more complex control; not yet fully supported — flag early |
| EHV (Extra High Voltage) | Dedicated TSO line devices on-site | Dual command source (dedicated line vs API); contract flag switching |

# 2. How to Read This Document

Each scenario is documented in a standard card format. Fields marked [DEV] or [QA] require input from the development or QA team respectively. Fields marked ✅ CONFIRMED have been validated through PRD review or incident analysis.

## Scenario Card Template

| Field | Description |
| --- | --- |
| ID | Unique identifier (e.g., EGC-PROT-001) |
| Component | EGC / FCR-C / Adaptor / PCS |
| Category | Connectivity, Data Quality, Limits, Configuration, Solver, Grid Compliance |
| Applies To | BESS Standalone / FIP / DC-Coupled / EHV / All |
| Trigger Condition | What causes this behavior to activate |
| Threshold / Timer | Numerical threshold or timeout value (if applicable) |
| Behavior | What the system does when triggered |
| Output to BESS | Actual dispatch command or power output effect |
| Alarm / Notification | Email, log, SCADA alarm, or none |
| Recovery Condition | What must happen for normal operation to resume |
| Interaction Risk | Known interactions with other protections that may compound |
| Diagnostic Clues | What O&M should look for in logs / data to confirm this scenario |
| Known Incidents | Reference to past incidents where this was observed |
| Status | Implemented / Planned / Under Review |

# 3. EGC Protection Scenarios

## 3.1 Connectivity Loss

### EGC-PROT-001: Internet / Cloud Connectivity Loss

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Connectivity |
| Applies To | All |
| Trigger Condition | EGC loses connection to EnOS cloud platform |
| Threshold / Timer | [1.Entering Failsafe in 5min(default value,configurable) |
| Behaviour | - EGC continue last schedule(No FCR) - BESS and PV to 0kW, and sends BESS stop command (FCR) |
| Output to BESS | - Keep the schedule BS.SysAPSetPoint value(No FCR) - 0kW(FCR) |
| Alarm / Notification | - Can check the Edge-Cloud Connection in Dev-portal. - Can configure the Email Alarm |
| Recovery Condition | Automatically resume cloud commands on reconnect |
| Interaction Risk | If FCR is active, does FCR-C continue independently during cloud loss? |
| Diagnostic Clues | Check Adaptor connection logs; EnOS heartbeat timestamps |
| Known Incidents | — |
| Status | [DEV] Implemented |

### EGC-PROT-002: EGC–Adaptor Communication Loss

| Field | Value |
| --- | --- |
| Component | EGC + Adaptor |
| Category | Connectivity |
| Applies To | All |
| Trigger Condition | EGC cannot communicate with the Enflex Adaptor |
| Threshold / Timer | 5Min(default value, configurable) |
| Behaviour | ✅ CONFIRMED (EGC4001): Configurable via parameter switch. Type 1 (legacy): EGC outputs per device default/safety setting. Type 2 (new): EGC p. |
| Output to BESS | Type 1: device default. Type 2: 0 kW setpoint + stop command |
| Alarm / Notification | EGC log Cloud Point (Alarm needs to be configured) |
| Recovery Condition | Automatic on Adaptor reconnect |
| Interaction Risk | FCR parameters are relayed via Adaptor — loss may also trigger FCR-PROT-001. Under Type 2, BESS stop means FCR also ceases; aggregator must be aware of this. |
| Diagnostic Clues | Adaptor process status; EGC–Adaptor heartbeat; check which Type is configured |
| Known Incidents | — |
| Status | ✅ Type 2 parameter confirmed in EGC4001 PRD (Jan 2026) |

Open Question: For FIP sites, when Type 2 activates (BESS stop), does PV PCS also stop? Or does PV continue generating, potentially causing reverse power flow? This must be coordinated with EGC-PROT-013 (Reverse Power Flow Prevention).

### EGC-PROT-003: BESS Disconnection Detection (15-Minute Timeout)

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Connectivity |
| Applies To | All |
| Trigger Condition | ANY ONE of four monitored data points has no reading for >15 minutes |
| Threshold / Timer | 15 minutes (per data point, independently monitored) |
| Monitored Points | BS.MaxChargePower, BS.MaxDischargePower, BS.CtrlState, BS.ActivePW |
| Behaviour | EGC treats the BESS as disconnected; overrides BS.ActivePW to 0 kW regardless of actual PCS reading |
| Output to BESS | No command |
| Alarm / Notification | - EGC log can see the alarm info - Dev-portal Edge Application Edge Grid Controller Running Status |
| Recovery Condition | When get the BS.CtrlState, BS.ActivePW point, EGC will automatically resume |
| Interaction Risk | CRITICAL — If BS.MaxChargePower has incorrect sign AND this protection activates, optimisation engine may produce oscillating dispatch. See Nogi Issue No.3. Internal load miscalculation compounds the effect. |
| Diagnostic Clues | Check data gaps in BS.MaxChargePower/BS.MaxDischargePower/BS.CtrlState/BS.ActivePW; look for EGC target dropping to near-zero simultaneously with PCS still reporting power |
| Known Incidents | Nogi FCR Issue No.3 (Nov 14, 2025) — 2000 kW oscillation caused by this protection + sign error |
| Status | Implemented (but interaction risks partially mitigated) |

Open Questions for Dev: (1) Is the 15-minute timeout configurable per site, or hardcoded? (2) When this protection activates, is there a log entry or state flag that O&M can query? (3) Should the timeout be shorter (e.g., 5 minutes) to surface issues faster, or would that cause false positives? (4) Is there a “partial disconnection” state, or is it binary?

Answer:

## 3.2 Data Quality & Abnormality

### EGC-PROT-004: Southbound BESS Telemetry — Invalid / Out-of-Range Values

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Data Quality |
| Applies To | All |
| Trigger Condition | BS.MaxChargePower or BS.MaxDischargePower value received is invalid, negative (when positive expected), or outside configured range |
| Threshold / Timer | [DEV] Is there a valid range check? What are the bounds? |
| Behaviour | [DEV] Does EGC: (a) reject and use last valid value, (b) reject and enter safe mode, (c) accept the value as-is? Not support |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] Is a data quality alarm raised? |
| Recovery Condition | [DEV] Automatic on valid data resumption? |
| Interaction Risk | Nogi Issue No.3 demonstrated that incorrect sign on BS.MaxChargePower (-1999 instead of +1999) was NOT rejected by EGC and caused optimisation engine to produce oscillating commands. This suggests there is currently no range/sign validation. |
| Diagnostic Clues | Check raw BS.MaxChargePower values for sign or magnitude anomalies |
| Known Incidents | Nogi Issue No.3 — BS.MaxChargePower = -1999 kW was accepted without alarm |
| Status | [DEV] Is input validation now implemented post-Nogi fix? Not support |

### EGC-PROT-005: Southbound BESS Telemetry — Missing, Stale, or Bad Quality

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Data Quality |
| Applies To | All |
| Trigger Condition | BESS telemetry data is missing, not updating (stale), or flagged as bad quality Can’t read BS.CtrlState |
| Threshold / Timer | 15 minutes (per data point, independently monitored) |
| Behaviour | BS.MaxChargePower, BS.MaxDischargePower, BS.CtrlState, BS.ActivePW |
| Output to BESS | EGC treats the BESS as disconnected; overrides BS.ActivePW to 0 kW regardless of actual PCS reading |
| Alarm / Notification | No command |
| Recovery Condition | 1. |
| Interaction Risk | Stale data that persists >15 min will eventually trigger EGC-PROT-003 (BESS disconnection). The question is whether there is any intermediate action before the 15-minute cliff. |
| Diagnostic Clues | Compare data timestamps vs wall clock; look for frozen values |
| Known Incidents | Nogi Issue No.3 (data outage from FCR-C read/write conflict) |
| Status | Implemented |

## 3.3 Fail-Safe Mode

### EGC-PROT-006: EGC Enters Fail-Safe Mode

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Fail-Safe |
| Applies To | All |
| Trigger Condition | Check the “EGC Fail-Safe Complete List of Conditions” below |
| Threshold / Timer | Failsafe Condition can be configured in Failsafe Strategy |
| Behaviour | EGC outputs power according to device default/safety setting |
| Output to BESS | Configure in Failsafe Action, x% of BESS Power |
| Alarm / Notification | - EGC log can see the alarm info - Dev-portal Edge Application Edge Grid Control Running Status |
| Recovery Condition | Will automatically resume, return to the strategy configuration |
| Interaction Risk | [DEV] |
| Diagnostic Clues | NO fail-safe state flag in telemetry? NO |
| Known Incidents | — |
| Status | [DEV] Implemented |

- EGC Fail-Safe Complete List of Conditions

This document provides a comprehensive list of all conditions that cause EGC to enter fail-safe mode, including the newly added Extra High Voltage fail-safe function(no.6).

Document Version: 1.2  |  date: 2026-04-11  |  Total Fail-Safe Conditions: 11

Complete Fail-Safe Condition List

| Category | Fail Safe Name | Trigger Condition | Output Result | Output Result (Optional) | UI Config | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
| Load / Capacity | 1. Abnormal Load Drop | When EGC detects that site load power drops by more than abnormal drop threshold | Device outputs according to configured safety setting (e.g., BESS power = 0) | BESS Stop / PV Stop; | Yes | Configurable via Abnormal Drop Threshold setting |
|  | 2. Site Overcapacity Protection - Export | Past 5-minute average export power to grid exceeds export limitation (detection period < 1min) | Device outputs according to configured safety setting (e.g., BESS power = 0) | BESS Stop / PV Stop; | Yes | Includes dynamic export limitation option based on Curtailment plan. Fixed value retention with dynamic value switch (default OFF). Updated logic using difference between export and curtailment limit |
|  | 3. Site Overcapacity Protection - Import | Past 5-minute average import power from grid exceeds import limitation (detection period < 1min) | Same as above | BESS Stop / PV Stop; | No | Fixed value setting only, no dynamic value required |
| Communication | 4. Grid Meter Disconnection | Grid Meter is not connected (communication interrupted for certain period) | Device outputs according to configured safety setting | N/A | No | Communication status monitoring |
|  | 5. EGC-Enflex Disconnection | EGC communication with Enflex is lost (no heartbeat) for timeout period (default 5 minutes, configurable) | Device outputs according to configured safety setting, Fcr mode=off | BESS Stop / PV Stop; | No | Timeout default: 5 minutes, configurable |
|  | 6. Extra High Voltage Fail-Safe (NEW) | EGC communication with dedicated line device is lost (no heartbeat) for timeout period (default 5 minutes, configurable) | Same as EGC-Enflex disconnection. | BESS Stop / PV Stop; | No | Similar to EGC-Enflex disconnection. Timeout default: 5 minutes, configurable. Triggered when dedicated line device heartbeat has no value |
| Device / Status | 7. Sub-Device Disconnection | Sub-device is disconnected | Device outputs according to configured safety setting | N/A | No | Hardware/device status based |
| System / Internal | 8. FCR Parameter Parse Error | FCR parameter parsing error occurs | Device outputs according to configured safety setting, Fcr mode=off | N/A | No | System error detection |
|  | 9. EGC Solution Failure | EGC solving fault (e.g., MaxChargePower measurement point shows negative value) | Device outputs according to configured safety setting | N/A | No | Internal calculation/logic error |
| Configuration | 10. Power Curtailment File Exception | Power curtailment file is abnormal/exception | Device outputs according to configured safety setting | N/A | No | File/plan integrity issue |
|  | 11. No Power Plant Plan | No Power Plant Plan available (Curtailment Strategy) | Same as above | N/A | No | Missing plan configuration |

Summary by Category

| Category | Count | Fail-Safe Conditions |
| --- | --- | --- |
| Communication | 3 | Grid Meter Disconnection, EGC-Enflex Disconnection, Extra High Voltage Fail-Safe (NEW) |
| Load / Capacity | 3 | Abnormal Load Drop, Site Overcapacity Protection (Export & Import) |
| Device / Status | 1 | Sub-device Disconnection |
| System / Internal | 2 | FCR Parameter Parse Error, EGC Solution Failure |
| Configuration | 2 | Power Curtailment File Exception, No Power Plant Plan |
| Total | 11 |  |

Fail-Safe Behavior Notes

Output Behavior

- All fail-safe conditions trigger the same basic output: Device outputs power according to device default/safety setting

- The specific output values (e.g., BESS power = 0) can be configured in Failsafe Action settings

- Additional outputs: BESS Stop / PV Stop (model points BS.Stop, ESS.stopSet)

Recovery Mechanism

- EGC will automatically resume and return to normal strategy configuration when trigger condition is resolved

Configuration Notes

- Timeout settings: no.5,6 EGC-Enflex and Extra High Voltage fail-safe both have configurable timeout (default 5 minutes)

- Overcapacity protection: Supports both fixed export/import limitation and dynamic export limitation based on Curtailment schedule

- Stop command retry: Enhanced mechanism to handle PCS execution delay with configurable number of Stop command attempts

- Dynamic value switch: Overcapacity export limitation can use fixed value (default) or dynamic value based on Curtailment plan ratio

Alarm and Notification

- EGC log contains alarm information for all fail-safe triggers

- Dev-portal Edge Application shows EGC Grid Control Running Status

### EGC-PROT-007: Abnormal Load Drop

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Fail-Safe |
| Applies To | All |
| Trigger Condition | Sudden abnormal drop in site load |
| Threshold / Timer | [DEV] What constitutes “abnormal”? Rate of change? Absolute threshold? When the microgrid controller detects that the load power drops by more than the abnormal drop threshold, the failsafe action is executed. |
| Behaviour | Configure in Failsafe Action, x% of BESS Power |
| Output to BESS | EGC log can see the alarm info |
| Alarm / Notification | - Dev-portal Edge Application Edge Grid Control Running Status |
| Recovery Condition | [DEV] Will automatically resume, return to the strategy configuration |
| Interaction Risk | [DEV] |
| Diagnostic Clues | Load profile vs historical baseline; grid meter readings |
| Known Incidents | — |
| Status | [DEV] Implemented |

### EGC-PROT-008: Export Limitation Breach (BESS Standalone)

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Grid Compliance |
| Applies To | BESS Standalone |
| Trigger Condition | Average grid export power over the past 5 minutes exceeds the export limitation |
| Threshold / Timer | 5-minute rolling average exceeding configured export limit |
| Behaviour | EGC enters fail-safe; outputs per device default/safety setting. Optionally can trigger a stop command for BESS. |
| Output to BESS | [DEV] Stop command? Ramp down? Same as EGC-PROT-006, failsafe mode |
| Alarm / Notification | [DEV] Same as EGC-PROT-006 |
| Recovery Condition | [DEV] Automatic when export returns below limit? Hysteresis? Same as EGC-PROT-006 |
| Interaction Risk | If FCR is active and injecting power, does the export limitation override FCR dispatch? |
| Diagnostic Clues | 5-minute rolling average vs export limit configuration |
| Known Incidents | — |
| Status | [DEV] Implemented |

## 3.4 Solver & Optimisation Errors

### EGC-PROT-009: EGC Solver Failure

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Solver |
| Applies To | All |
| Trigger Condition | Optimisation engine fails to converge or produces infeasible result (e.g., MaxChargePower measurement is negative when positive expected) |
| Threshold / Timer | [DEV] How many consecutive solver failures before fail-safe? Immediate? Immediate |
| Behavior | EGC outputs per device default/safety setting |
| Output to BESS | [DEV] 0kW |
| Alarm / Notification | [DEV] - EGC log can see the alarm info - Dev-portal Edge Application Edge Grid Control Running Status |
| Recovery Condition | [DEV] Does solver auto-retry each cycle? Will auto-retry each cycle |
| Interaction Risk | Solver failure with stale inputs may produce unexpected dispatch. Nogi oscillation was effectively a solver producing “correct” but dangerous output from wrong inputs. |
| Diagnostic Clues | Solver logs; check input values for sign/range anomalies |
| Known Incidents | Nogi Issue No.3 (solver produced oscillating output from negative MaxChargePower) |
| Status | [DEV] Implemented |

### EGC-PROT-010: Internal Load Calculation Anomaly

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Solver |
| Applies To | All (formula varies by topology) |
| Trigger Condition | Calculated internal load deviates significantly from expected range (e.g., jumps from ~40 kW to ~1900 kW) |
| Threshold / Timer | ✅ CONFIRMED (EGC4006 PRD): Max and min internal load constraints to be added per Yasuoka-san’s feedback. [DEV] What are the constraint values? |
| Behaviour | ✅ CONFIRMED (EGC4006 PRD): Load smoothing filter to be applied. Yasuoka-san recommends always-on smoothing (no enter/exit mode) to avoid extra failure handling complexity. Dev lead Yintao evaluating PID vs α-coefficient approach. |
| Load Calc by Topology | BESS Standalone: Load = Grid Meter − BS.ActivePW. FIP (PV+BESS) daytime: Load = ActivePower(PV+BESS) − Grid Meter. FIP nighttime (PV=0): Behaves same as BESS Standalone. |
| Output to BESS | Smoothed dispatch; transients clamped within configurable min/max bounds |
| Alarm / Notification | [DEV] Should there be an alarm when load value is clamped? EGC log |
| Recovery Condition | Self-correcting via filter; no manual intervention expected |
| Interaction Risk | This is the root mechanism of the Nogi oscillation. Grid meter and PCS response speed differences make this a systemic risk across all OEMs. Filter must be validated per OEM. |
| Diagnostic Clues | Compare calculated internal load vs expected (~30–50 kW for typical sites); check timing alignment between grid meter and PCS Modbus updates; use EGC4004 200ms datalog for detailed analysis |
| Known Incidents | Nogi Issue No.3, FCR Controller timing mismatch (Dec 2025 session) |
| Status | IN PROGRESS — EGC4006 PRD under review; targeting release with Huawei SACU |

Kevin’s note (Jan 28): Frankie’s approach to calculate internal load in hybrid plants is fine. The filter should stabilise the transients from PCS delay. However, for DC-coupled hybrid projects, the control is much more complex (PV curtailment, charging ESS using grid power, etc.) — we should be prepared for this even if it’s not the immediate priority.

## 3.5 SOC Limits

### EGC-PROT-011: SOC Upper Limit Reached

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Limits |
| Applies To | All |
| Trigger Condition | BESS state of charge reaches configured upper SOC limit |
| Threshold / Timer | [DEV] What is the default upper SOC limit? Is it configurable per site? 100% by default, also can configure in BESS plan |
| Behaviour | [DEV] Stop charging? Allow discharge only? Reduce charge rate gradually? Stop charging |
| Output to BESS | [DEV] 0kW |
| Alarm / Notification | [DEV] No |
| Recovery Condition | [DEV] SOC drops below limit minus hysteresis? Can charge and discharge |
| Interaction Risk | If FCR is active and frequency is low (requiring charge), does SOC limit override FCR? |
| Diagnostic Clues | SOC value vs configured limits |
| Known Incidents | — |
| Status | [DEV] Implemented |

### EGC-PROT-012: SOC Lower Limit Reached

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Limits |
| Applies To | All |
| Trigger Condition | BESS state of charge reaches configured lower SOC limit |
| Threshold / Timer | [DEV] 0% by default, also can configure in BESS plan |
| Behaviour | [DEV] Stop discharging? Allow charge only? Stop discharging |
| Output to BESS | [DEV] 0kW |
| Alarm / Notification | [DEV] No |
| Recovery Condition | [DEV] Can charge and discharge |
| Interaction Risk | If FCR is active and frequency is high (requiring discharge), does SOC limit override FCR? |
| Diagnostic Clues | SOC value vs configured limits |
| Known Incidents | — |
| Status | [DEV] Implemented |

## 3.6 FIP-Specific Protections (PV + BESS Sites)

These scenarios were confirmed during TSO test item review (Jan 2026) and formalised in the FIP modification PRD (EGC4001).

### EGC-PROT-013: Reverse Power Flow Prevention

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Grid Compliance |
| Applies To | FIP only |
| Trigger Condition | Power flowing from grid into site (reverse flow) detected at Grid Meter |
| Threshold / Timer | ✅ CONFIRMED: Threshold = the larger of: (a) renewable generator rated output × 1.05, or (b) +150 W. Configurable, single decimal place. Monitored every 1 minute. |
| Behaviour | [DEV] EGC reduces BESS charging? Curtails PV? Trips PCS? EGC reduces BESS charging |
| Output to BESS | [DEV] EGC reduces BESS charging |
| Alarm / Notification | [DEV] EGC log |
| Recovery Condition | [DEV] Automatic when flow direction normalises? Yes |
| Interaction Risk | If BESS is charging from grid (not permitted under FIP), this protection should fire. Interaction with EGC-PROT-014 (Renewable-Only Charging). |
| Diagnostic Clues | Grid meter power direction; check if BESS was charging while PV output was low |
| Known Incidents | — |
| Status | ✅ Specification confirmed (EGC4001 / FIP PRD) |

### EGC-PROT-014: Renewable-Only Charging Guarantee

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Grid Compliance |
| Applies To | FIP only |
| Trigger Condition | Forward power flow (Grid → Plant) detected at Grid Meter during BESS charging, indicating BESS is being charged from grid rather than from renewable generation |
| Threshold / Timer | ✅ CONFIRMED: Forward-flow threshold = the larger of: (a) renewable generator rated output × 1.05, or (b) +150 W. Configurable, single decimal place. |
| Behaviour | Condition is flagged as abnormal. [DEV] Does EGC reduce BESS charge rate? Stop charging? Alert only? Same as EGC-PROT-013 |
| Output to BESS | [DEV] Same as EGC-PROT-013 |
| Alarm / Notification | [DEV] Same as EGC-PROT-013 |
| Recovery Condition | [DEV] Same as EGC-PROT-013 |
| Interaction Risk | During cloudy periods with fluctuating PV, brief reverse flow may cause false positives. Does the 1-minute monitoring interval provide sufficient smoothing? |
| Diagnostic Clues | Grid meter direction during BESS charge periods; PV output vs BESS charge rate |
| Known Incidents | — |
| Status | ✅ Specification confirmed (EGC4001 / FIP PRD) |

### EGC-PROT-015: FIP Stop Function (5-Minute Average Breach)

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Grid Compliance |
| Applies To | FIP only |
| Trigger Condition | 5-minute average of grid meter power (based on five consecutive 1-minute values) exceeds the allowable threshold |
| Threshold / Timer | ✅ CONFIRMED: 5-minute average of 1-minute Grid Meter readings |
| Behavior | ✅ CONFIRMED (updated Jan 21 per TSO review): PCS stop command applied to BOTH PV PCS AND BESS PCS (0 kW setpoint). Previously documented as BESS-only — now confirmed to include all PCS units. |
| Output to BESS | Fail safe:Site Overcapacity Protection - Export --0 kW setpoint + stop command to all PCS (PV + BESS) |
| Recovery Condition | ✅ CONFIRMED: Automatic reboot is NOT allowed. Reboot must be manual. |
| Alarm / Notification | [DEV] Is an alarm sent when this triggers? Critical for O&M to know site is stopped. EGC log Cloud point (EGC write an alarm point ,Need to configure on CAI) |
| Interaction Risk | CRITICAL — Once triggered, entire site stops (PV + BESS). No automatic recovery. O&M must be alerted immediately. If alarm is missing or delayed, site sits idle indefinitely. |
| Diagnostic Clues | 5-minute rolling average calculation; all PCS at 0 kW; manual restart required |
| Known Incidents | — |
| Status | ✅ Specification confirmed; scope expanded to PV PCS per TSO review (Jan 21, 2026) |

IMPORTANT: This is a TSO-mandated safety function. The “no automatic reboot” requirement means O&M procedures must include monitoring for this event and rapid manual response. Any delay = lost revenue from both PV and BESS.

## 3.7 EHV-Specific Scenarios (Extra High Voltage Sites)—To input after April after MVP dev is done

### EGC-PROT-016: Dedicated Line vs API Command Source Conflict

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Configuration / Command Routing |
| Applies To | EHV only |
| Trigger Condition | EGC receives conflicting kW commands from both the dedicated TSO line and the API simultaneously, or the contract flag (EDC/LFC ON/OFF) is in an unexpected state |
| Threshold / Timer | [DEV] |
| Behaviour | [DEV] EGC switches source based on contract flags. What happens if flags are contradictory or missing? |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] |
| Recovery Condition | [DEV] |
| Interaction Risk | FCR commands always come via API (never dedicated line). But if EGC is in dedicated-line mode and receives an FCR API command, which takes priority? |
| Diagnostic Clues | Check EDC/LFC flag states; compare dedicated line commands vs API commands |
| Known Incidents | — |
| Status | [DEV] Dev in March 2026 |

### EGC-PROT-017: Dedicated Line Communication Loss

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Connectivity |
| Applies To | EHV only |
| Trigger Condition | Communication with TSO dedicated line device is lost |
| Threshold / Timer | [DEV] |
| Behaviour | [DEV] Does EGC fall back to API commands? Hold last dedicated line value? Enter safe mode? |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] |
| Recovery Condition | [DEV] |
| Interaction Risk | If TSO expects dedicated-line response and it’s lost, TSO may independently trip the site. EGC behaviour must align with TSO expectations. |
| Diagnostic Clues | Dedicated line heartbeat; Remote IO status |
| Known Incidents | — |
| Status | [DEV] Dev in March 2026 |

### EGC-PROT-018: Curtailment Device (CDT) Command Handling

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Grid Compliance |
| Applies To | EHV only |
| Trigger Condition | TSO curtailment (export control) command received via CDT device |
| Threshold / Timer | [DEV] |
| Behaviour | [DEV] How does EGC reconcile curtailment with existing FCR/JEPX dispatch? |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] |
| Recovery Condition | [DEV] Automatic when curtailment is lifted? |
| Interaction Risk | Curtailment + FCR: if curtailed but FCR requires discharge, which wins? |
| Diagnostic Clues | CDT command log; grid export vs curtailment limit |
| Known Incidents | — |
| Status | [DEV] Dev in March 2026 |

# 4. FCR Controller Scenarios

### FCR-PROT-001: FCR Controller Receives Incomplete Parameters from Adaptor

| Field | Value |
| --- | --- |
| Component | FCR-C (via EGC) |
| Category | Configuration |
| Applies To | All FCR-enabled sites |
| Trigger Condition | FCR parameters from Adaptor are incomplete (e.g., missing droop coefficient, contracted kW, or frequency deadband) |
| Threshold / Timer | [DEV] Immediate rejection? Or attempt with defaults? Immediately |
| Behavior | Fail safe-- FCR Parameter Parse Error |
| Output to BESS | [DEV] 0kW |
| Alarm / Notification | [DEV] EGC log Cloud point (to do Alarm needs to be configured) |
| Recovery Condition | [DEV] Automatic on receipt of valid parameters? Yes |
| Interaction Risk | If FCR falls back to safe mode but baseline EGC dispatch continues, the aggregator may not realise FCR is inactive |
| Diagnostic Clues | Check FCR parameter payload from Adaptor; validate completeness |
| Known Incidents | — |
| Status | [DEV] Implemented |

### FCR-PROT-002: FCR Controller Read/Write Conflict

| Field | Value |
| --- | --- |
| Component | FCR-C |
| Category | Data Quality |
| Applies To | Sites with SCADA-EMS FCR controller |
| Trigger Condition | FCR controller cannot perform simultaneous read and write on Modbus, causing data gaps in monitored points |
| Threshold / Timer | N/A (design issue — now fixed) |
| Behavior | Intermittent data outages for BS.MaxChargePower and other points; if gap >15 min, triggers EGC-PROT-003 |
| Output to BESS | No direct effect until EGC-PROT-003 cascades |
| Alarm / Notification | None (this was the problem — silent failure) |
| Recovery Condition | FCR controller reconfigured to support simultaneous read/write |
| Interaction Risk | Direct trigger for EGC-PROT-003 → EGC-PROT-009/010 cascade |
| Diagnostic Clues | Data gaps in BS.MaxChargePower timeline |
| Known Incidents | Nogi Issue No.3 |
| Status | ✅ COMPLETED (fix deployed) |

### FCR-PROT-003: Grid Meter / PCS Timing Mismatch

| Field | Value |
| --- | --- |
| Component | FCR-C + EGC |
| Category | Timing / Latency |
| Applies To | All |
| Trigger Condition | Response-speed difference between grid meter updates and PCS Modbus register updates causes internal load calculation error |
| Threshold / Timer | Observed: ~1,166 ms lag between grid meter and PCS readings |
| Behaviour | Calculated internal load spikes transiently, causing incorrect dispatch for one or more control cycles |
| Output to BESS | Transient over/under-dispatch; magnitude depends on BESS capacity and timing delta |
| Alarm / Notification | [DEV] Currently none. Should there be a timing-quality alert? No |
| Recovery Condition | Self-correcting on next cycle if timing realigns; systemic if OEM response speed differs fundamentally |
| Interaction Risk | Compounds with EGC-PROT-010. Worse with higher-capacity BESS (larger transient error). |
| Diagnostic Clues | Compare grid meter timestamp vs PCS data timestamp at 50ms resolution; look for calculated load > 2× expected. Use EGC4004 200ms datalog for detailed analysis. |
| Known Incidents | Dec 2025 Japan session — identified as systemic risk across OEMs |
| Status | Short-term: EGC4006 load filter (IN PROGRESS). Long-term solution TBD. |

### FCR-PROT-004: FCR 2-Point Calculation Debugging (EGC-Based FCR)

| Field | Value |
| --- | --- |
| Component | EGC (with FCR on EGC) |
| Category | Debugging / Observability |
| Applies To | Sites using FCR on EGC (not SCADA-EMS) |
| Trigger Condition | N/A — this is a diagnostic capability, not a protection |
| Threshold / Timer | N/A |
| Behaviour | ✅ CONFIRMED (EGC4008): EGC performs FCR 2-point calculation internally for debugging comparison |
| Open Question | [DEV] Can EGC acquire frequency data point from all 3rd-party FCR controllers (SCADA EMS, SPPC)? Yes |
| Diagnostic Clues | Compare EGC’s internal FCR calculation with actual FCR-C output |
| Known Incidents | — |
| Status | EGC4008 PRD under review |

# 5. Enflex Adaptor Scenarios

### ADPT-PROT-001: Aggregator Communication Interruption (Unrecovered >5 min)

| Field | Value |
| --- | --- |
| Component | Adaptor |
| Category | Connectivity |
| Applies To | All |
| Trigger Condition | Communication with Aggregator system not recovered for 5 minutes |
| Threshold / Timer | 5 minutes |
| Behaviour | Triggers email alarm |
| Output to BESS | [DEV] Does EGC continue with last received schedule, or enter safe mode? |
| Alarm / Notification | Email alarm |
| Recovery Condition | [DEV] Automatic on reconnect? |
| Interaction Risk | If aggregator connection lost during FCR contract period, does FCR continue with last parameters? |
| Diagnostic Clues | Adaptor connection logs; aggregator API response codes |
| Known Incidents | — |
| Status | [DEV] |

### ADPT-PROT-002: Invalid API Payload from Aggregator

| Field | Value |
| --- | --- |
| Component | Adaptor |
| Category | Data Quality |
| Applies To | All |
| Trigger Condition | [DEV] Malformed JSON? Missing required fields? Out-of-range values? |
| Threshold / Timer | [DEV] |
| Behaviour | [DEV] Reject command and log error? Accept partial? Use last valid? |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] |
| Recovery Condition | [DEV] |
| Interaction Risk | [DEV] |
| Diagnostic Clues | Adaptor ingestion logs; API payload validation errors |
| Known Incidents | — |
| Status | [DEV] |

### ADPT-PROT-003: Aggregator Service Unreachable

| Field | Value |
| --- | --- |
| Component | Adaptor |
| Category | Connectivity |
| Applies To | All |
| Trigger Condition | [DEV] DNS failure? HTTP timeout? TLS certificate error? |
| Threshold / Timer | [DEV] Retry logic? Backoff? |
| Behaviour | [DEV] |
| Output to BESS | [DEV] |
| Alarm / Notification | [DEV] |
| Recovery Condition | [DEV] |
| Interaction Risk | Similar to ADPT-PROT-001 but may have different retry behaviour |
| Diagnostic Clues | Network-layer logs; HTTP response codes |
| Known Incidents | — |
| Status | [DEV] |

# 6. Additional Edge-Case Scenarios

These scenarios represent edge cases that could surface as we scale to 90 projects with diverse OEMs and site configurations. They were not in the initial structure and were added based on incident analysis and scaling risk assessment.

### EDGE-001: Partial PCS Fleet Failure (Multi-PCS Sites)

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Equipment |
| Applies To | All multi-PCS sites |
| Trigger Condition | One or more PCS units trip or go offline while others remain operational |
| Threshold / Timer | [DEV] Checking in every cycle |
| Behavior | [DEV] Does EGC redistribute load across remaining PCS? Does it recalculate MaxChargePower / MaxDischargePower dynamically? Or does it treat the entire BESS as degraded? 1. Multiple PCS, if one PCS is broken, the remaining ones will be recalculated. 2. With a Huawei controller controlling multiple PCS, it treats the entire BESS as degraded. |
| Interaction Risk | If EGC doesn’t recalculate capacity, it may dispatch beyond the remaining PCS capability, causing overload or further trips. If an FCR contract is active, contracted kW may exceed available capacity. |
| Diagnostic Clues | Individual PCS status; total available capacity vs dispatch target |
| Known Incidents | — |
| Status | [DEV] |

### EDGE-002: Configuration Parameter Error (Wrong Value Deployed)

| Field | Value |
| --- | --- |
| Component | EGC / FCR-C |
| Category | Configuration |
| Applies To | All |
| Trigger Condition | A site configuration parameter is set to an incorrect value (e.g., wrong sign, wrong unit, wrong site capacity) — not caught by validation |
| Threshold / Timer | N/A — depends on when the error manifests |
| Behaviour | Unpredictable — depends on which parameter is wrong. Nogi sign error is one example. |
| Interaction Risk | HIGH — configuration errors are the most common root cause of unexpected behaviour. They bypass all runtime protections because the protection logic trusts its own config. |
| Diagnostic Clues | Compare deployed config vs design spec; look for values that seem correct individually but produce wrong system behaviour |
| Known Incidents | Nogi Issue No.3 (BS.MaxChargePower sign) |
| Status | [DEV] Is there a config validation/review step in the deployment process? Not support |

Suggestion: Implement a deployment config validation script that checks all critical parameters against expected ranges and signs before a site goes live. This would have caught the Nogi sign error.

### EDGE-003: NTP / Time Synchronization Failure

| Field | Value |
| --- | --- |
| Component | EGC / FCR-C |
| Category | Infrastructure |
| Applies To | All |
| Trigger Condition | EGC or FCR controller loses NTP synchronization, or clock drifts significantly |
| Threshold / Timer | [DEV] Is NTP status monitored? What drift is tolerable? |
| Behaviour | [DEV] Schedule execution may fire at wrong times; TSO pre-assessment 200ms logs may have inaccurate timestamps; FCR response timing may fail compliance checks Not support |
| Interaction Risk | FCR compliance is measured in sub-second resolution. Clock drift of even 1–2 seconds could cause a passing response to appear non-compliant, or vice versa. EGC4004 200ms datalog depends on accurate timestamps. |
| Diagnostic Clues | Compare EGC timestamps vs external reference; NTP daemon status |
| Known Incidents | — |
| Status | [DEV] Not support |

### EDGE-004: BESS Thermal Protection / Temperature Limit

| Field | Value |
| --- | --- |
| Component | PCS (southbound) |
| Category | Equipment |
| Applies To | All |
| Trigger Condition | BESS or PCS reaches thermal limit and unilaterally reduces available power or trips |
| Threshold / Timer | OEM-specific; managed at PCS level |
| Behaviour | [DEV] Does EGC receive a signal that available capacity has been reduced? Or does it discover this when its dispatch command is not followed? Not support |
| Interaction Risk | If EGC dispatches 2000 kW but PCS has thermally derated to 1500 kW, the 500 kW gap appears as a control error. Aggregator may penalise for non-delivery. FCR compliance may fail. |
| Diagnostic Clues | PCS temperature readings; BS.MaxChargePower / BS.MaxDischargePower vs rated values; dispatch target vs actual output gap |
| Known Incidents | — |
| Status | [DEV] Does EGC read thermal derating signals from any OEM? Not support |

### EDGE-005: Concurrent Schedule + Real-Time Command Conflict

| Field | Value |
| --- | --- |
| Component | EGC / Adaptor |
| Category | Command Routing |
| Applies To | All |
| Trigger Condition | Aggregator sends a real-time (ad-hoc) control command while a pre-set schedule is active, and the commands conflict |
| Threshold / Timer | [DEV] |
| Behaviour | [DEV] Which takes priority — schedule or real-time? Is there a defined priority hierarchy? What happens at the boundary when the real-time command expires? Use the latest schedule |
| Interaction Risk | Ambiguity here causes unpredictable site behavior. Aggregators need to understand the priority rules to avoid surprises. |
| Diagnostic Clues | Check schedule timeline vs real-time command log; look for conflicting timestamps |
| Known Incidents | — |
| Status | [DEV] Implemented |

### EDGE-006: EGC Software Crash / Restart

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Infrastructure |
| Applies To | All |
| Trigger Condition | EGC process crashes or is restarted (planned or unplanned) |
| Threshold / Timer | [DEV] Auto-restart time? Watchdog timer? Watchdog timer, EGC will restart in 2 min. |
| Behaviour | [DEV] What is the PCS behavior when EGC stops sending commands? Does PCS hold last setpoint? Ramp to zero? What about during EGC boot — does it resume from last state or start fresh? PCS hold last setpoint. EGC will start fresh. |
| Interaction Risk | If PCS holds last setpoint during EGC restart, and that setpoint was +2000 kW discharge, the BESS continues discharging uncontrolled until EGC comes back. |
| Diagnostic Clues | EGC process uptime; system logs; gap in dispatch commands |
| Known Incidents | — |
| Status | [DEV] Implemented |

### EDGE-007: Simultaneous Multiple Protection Activation

| Field | Value |
| --- | --- |
| Component | EGC |
| Category | Interaction |
| Applies To | All |
| Trigger Condition | Two or more protection mechanisms activate simultaneously (e.g., SOC limit + export limit + adaptor communication loss) |
| Threshold / Timer | N/A |
| Behaviour | [DEV] Is there a defined priority order for protections? Does the most restrictive win? Or does the first-activated lock out others? No priority, If a condition is triggered, it goes into failsafe |
| Interaction Risk | Without a defined priority hierarchy, the outcome of simultaneous protections is unpredictable. This is the class of issue that caused Nogi. |
| Diagnostic Clues | Multiple protection flags active simultaneously in logs |
| Known Incidents | Nogi Issue No.3 (EGC-PROT-003 + EGC-PROT-004 + EGC-PROT-010 simultaneous) |
| Status | [DEV] Implemented |

Critical question for Dev: Define a protection priority hierarchy — e.g.: (1) Grid compliance (export limit, FIP stop function) — highest. (2) Equipment safety (SOC limits, thermal). (3) Connectivity protections (disconnection, adaptor loss). (4) Data quality protections (stale data, invalid values). Without this hierarchy, we cannot predict system behaviour when multiple conditions occur together.

# 7. Interaction Matrix

One of the key lessons from the Nogi incident is that individual protection can cascade. This matrix identifies dangerous combinations that must be tested and documented.

| Trigger A | Trigger B | Combined Effect | Severity | Documented? |
| --- | --- | --- | --- | --- |
| EGC-PROT-003 (BESS disconnection) | EGC-PROT-004 (sign error on MaxChargePower) | Oscillating dispatch commands; 2000 kW swings | CRITICAL | Yes (Nogi No.3) |
| EGC-PROT-003 (BESS disconnection) | EGC-PROT-010 (internal load anomaly) | Phantom load causes incorrect compensation dispatch | HIGH | Yes (Nogi No.3) |
| FCR-PROT-003 (timing mismatch) | EGC-PROT-010 (internal load anomaly) | Transient dispatch error on every control cycle | MEDIUM | Yes (Dec 2025) |
| EGC-PROT-002 Type 2 (Adaptor loss → BESS stop) | EGC-PROT-013 (Reverse power flow) | FIP: BESS stops but PV continues → possible reverse flow if PV > load | HIGH | No |
| EGC-PROT-015 (FIP 5-min stop) | Any other protection | Site is fully stopped (PV+BESS); no auto recovery. If operator doesn’t notice, other protections are moot. | CRITICAL | No |
| ADPT-PROT-001 (aggregator loss) | FCR-PROT-001 (incomplete FCR params) | [DEV] Does FCR fall back? Does EGC know? | [DEV] | No |
| EGC-PROT-008/015 (export limit) | FCR active (frequency response) | [DEV] Does export limit override FCR? | [DEV] | No |
| EGC-PROT-011/012 (SOC limits) | FCR active (frequency response) | [DEV] Does SOC limit override FCR dispatch? | [DEV] | No |
| EGC-PROT-001 (cloud loss) | FCR active | [DEV] Does FCR continue independently? | [DEV] | No |
| EDGE-001 (partial PCS failure) | FCR active | FCR contracted kW may exceed remaining capacity | HIGH | No |
| EDGE-004 (thermal derating) | EGC-PROT-010 (load anomaly) | Dispatch exceeds derated capacity → PCS doesn’t follow → load calc error amplifies | MEDIUM | No |
| EDGE-006 (EGC restart) | EGC-PROT-015 (FIP stop active) | After restart, does EGC know the FIP stop was active? Or does it try to resume? | HIGH | No |
| [DEV] | [DEV] | Add additional identified combinations | [DEV] | — |

# 8. Priority Classification

Each scenario should be rated by the Dev/QA team:

| Severity | Definition | Response Expectation |
| --- | --- | --- |
| CRITICAL | May cause equipment damage, grid code violation, or safety hazard | Immediate safe-state; alarm within seconds |
| HIGH | Significant operational impact; incorrect dispatch >10% of capacity | Safe-state within 1 control cycle; alarm within 1 minute |
| MEDIUM | Degraded performance; suboptimal dispatch | Log + alarm; continue with constrained operation |
| LOW | Minor deviation; self-correcting | Log only |

[DEV]: Please assign a severity rating to each scenario above.

# 9. Diagnostic Quick Reference

To be populated after Dev/QA completes the scenario cards.

For each scenario, O&M should be able to answer:

- What symptom did I observe? (e.g., “BESS output dropped to 0 unexpectedly”)

- Which scenario card matches? (look up by symptom → scenario ID)

- What data should I check? (per diagnostic clues in the card)

- Is this expected behaviour or a bug? (per documented behavior)

- What is the recovery path? (per recovery condition)

## Symptom-to-Scenario Lookup Table

| Symptom | Likely Scenario(s) | First Check |
| --- | --- | --- |
| BESS output drops to 0, no alarm | EGC-PROT-003, EGC-PROT-006 | Check BS.* data point gaps in last 15 min |
| Power oscillation (rapid charge/discharge) | EGC-PROT-003 + EGC-PROT-004 | Check BS.MaxChargePower sign and data gaps |
| Dispatch doesn’t match aggregator schedule | ADPT-PROT-001, ADPT-PROT-002, EDGE-005 | Check Adaptor connection status, API logs, real-time command log |
| Export limit breach despite EGC control | EGC-PROT-008, FCR-PROT-003 | Check 5-min rolling average vs limit; FCR output |
| Entire FIP site stops (PV + BESS at 0) | EGC-PROT-015 | Check 5-min average; manual restart required |
| BESS charging from grid at FIP site | EGC-PROT-014 | Check grid meter direction during BESS charge |
| Reverse power flow at FIP site | EGC-PROT-013 | Check grid meter direction; PV output vs load |
| BESS stops after Adaptor disconnect | EGC-PROT-002 (Type 2) | Check EGC–Adaptor connectivity; confirm Type 2 is configured |
| FCR response seems inactive | FCR-PROT-001, ADPT-PROT-001 | Check FCR parameter payload; Adaptor status |
| Transient dispatch spikes every control cycle | FCR-PROT-003, EGC-PROT-010 | Use 200ms datalog (EGC4004); compare grid meter vs PCS timing |
| BESS delivers less than dispatched | EDGE-001, EDGE-004 | Check individual PCS status; temperature readings |
| [DEV/QA] Add more symptoms | — | — |

# 10. Open Questions for Dev/QA Team

These are the highest-priority unknowns that need answers to make this document actionable:

## From v0.1 (Unchanged)

- Fail-safe definition: What exactly is the “device default/safety setting”? Is it 0 kW, last setpoint, or site-configurable? Does it differ between EGC-only, EGC+FCR, and FIP deployments?

- 15-minute timeout configurability: Is the BESS disconnection timeout (EGC-PROT-003) hardcoded or configurable? Can it be tuned per site based on OEM characteristics?

- Input validation: Post-Nogi, has sign/range validation been added for BS.MaxChargePower and BS.MaxDischargePower? If not, when is this planned?

- Intermediate staleness handling: Between “data is fresh” and “15-minute disconnection threshold,” does EGC take any intermediate action (e.g., flag, degrade, alarm)?

- FCR priority vs protection: When a protection mechanism activates (e.g., SOC limit, export limit), does it unconditionally override FCR dispatch? What is the priority hierarchy?

- State visibility: For each protection activation, is there a queryable state flag or telemetry point that O&M can check remotely, or must they infer from data patterns?

- Cloud loss + FCR: If cloud connectivity is lost while FCR is active, does FCR continue using last-received parameters indefinitely? Is there a maximum FCR autonomous duration?

## New in v0.2

- EGC-PROT-002 Type 2 + FIP: When Type 2 activates (BESS stop on Adaptor disconnect), does PV PCS also stop at FIP sites? If not, reverse power flow may occur.

- Load filter parameters (EGC4006): What are the final design choices — PID or α-coefficient? What are the min/max internal load constraints? Has Yasuoka-san’s recommendation (always-on, no enter/exit mode) been accepted?

- EGC-PROT-015 alarm: When the FIP 5-minute stop triggers, is there an immediate alarm to O&M? Given no auto-reboot, this is critical for revenue loss minimisation.

- Protection priority hierarchy: When multiple protections activate simultaneously, what is the execution order? (Proposed: grid compliance > equipment safety > connectivity > data quality)

- Config validation: Is there a deployment-time validation script that checks critical parameters (signs, ranges, site capacity) before a site goes live?

- EGC restart state persistence: After an EGC crash/restart, does it restore its pre-crash state (including active protections like FIP stop)? Or does it start fresh?

# 11. Revision Plan

| Milestone | Target Date | Owner |
| --- | --- | --- |
| Framework v0.2 review (this document) | Feb 16, 2026 | Kevin Zhang |
| Dev/QA populate all [DEV] fields | End of April 2026 | Frankie Fu, EGC Dev Team |
| Internal review & interaction matrix start | End-April 2026 | Kevin Zhang, Yasuoka-san |
| V1.0 release (internal reference) | Mid of May 2026 | Frankie Fu |
| Customer-facing summary (if applicable) | May 2026 | Kevin Zhang, Moroishi-san |

# Appendix A: Reference Incidents

| Incident ID | Date | Site | Summary | Scenarios Triggered |
| --- | --- | --- | --- | --- |
| Nogi FCR Issue No.3 | Nov 14, 2025 | Nogi (野木) | 2000 kW oscillation from FCR-C read/write conflict → 15-min data outage → disconnection protection + sign error | EGC-PROT-003, EGC-PROT-004, EGC-PROT-010, FCR-PROT-002 |
| [Add future incidents here] | — | — | — | — |

# Appendix B: PRD Cross-Reference

| PRD ID | Title | Related Scenarios |
| --- | --- | --- |
| EGC4001 | FIP modification | EGC-PROT-002, EGC-PROT-013, EGC-PROT-014, EGC-PROT-015 |
| EGC4004 | 200ms datalog for TSO pre-assessment | FCR-PROT-003 (diagnostic tool) |
| EGC4006 | Load filter formula on EGC | EGC-PROT-010 |
| EGC4007 | EGC on Moxa | N/A — Moxa hardware validation tracked within EGC4007 PRD scope |
| EGC4008 | FCR 2-point calculation on EGC for debugging | FCR-PROT-004 |

# Appendix C: Related Documents

| Document | Location | Notes |
| --- | --- | --- |
| EGC Trouble Shooting Guide | [Frankie to provide link] | Existing doc to be enhanced alongside this rule book |
| Nogi FCR Issue No.3 RCA Report | Internal | Root cause analysis referenced throughout |
| Aggregator Standard API Spec v3.5.6 | Internal | API-level command structure and feedback mechanisms |
| FCR Controller Control Logic (Dec 2025 Session) | Internal | Timing mismatch analysis and improvement roadmap |
| No.49 - FIP Related Modification (Nov) | Internal | TSO test item review; FIP protection specifications |